## Cover Page
Client
United Utilities - AX4 Program: System Integration.
Project Name: |  | Tyldesley UID PLC05 - Chemical Dosing |  | UU Site / Project Ref: |  | 80021608_02 |  | Date : | 2014-01-27
Cougar Project No. |  | 56938 |  | Client Ref: |  | WIG0179
Document Number: |  | WIG0179_80021608_01_20_61418
SDS Annexure
Revision History |  |  | Prepared By |  | Checked By |  | Submitted To
Date | Rev.No. | Details | Name | Organization | Name | Organization | Name | Organization
2014-01-27 | A1 |  | Greg McCormack | Cougar Automation | Ed Brown | Cougar Automation | Steve Kerrigan | BBUSL
Worksheets in this document :
No. | Name |  | Details
1 | Count Summary |  | I/O Count Summary
2 | Sys Arch Overview |  | System Architecture Overview
3 | Sys Arch Detailed |  | System Architecture Detailed
4 | PLC Power Calculation |  | PLC Power calculation
5 | PS Module Selection |  | Power Supply Selection
6 | PLC Bill of Material |  | PLC Bill of Material
7 | PLC#1 Harwired IO Count |  | Harwired I/O Schedule
8 | PLC#1 Soft IO Count |  | Soft I/O Schedule
9 | Network Load |  | Network Load Calculation
10 | Tag Database |  | PLC Tag Database
11 | Alarm Schedule |  | PLC Alarm Database
12 | PLC to PLC Comm |  | PLC to PLC Communication Data
13 | Siemens Telemetry PLC DB |  | Telemetry PLC Database
14 | AB PLC Telemetry DB |  | Telemetry PLC Database

## Count Summary
Project Title: United Utilities - Tyldesley UID PLC05 - Chemical Dosing
UUID: 80021608_02
Contract Title: System Integration
Document Title: Software Design Specification
SDS Annexure
I/O COUNT SUMMARY
| PLC No: | PLC # 5 ( Chemical Dosing )
| Model: | Siemens S7-300
No. | Tag type | Count as per tag details | Spare % | Spare Counts | Contingency count | Total count | No. of channels per module | Number of modules required
1 | Analogue Inputs (Normal) | 1 | 87.5 | 7 | 0 | 8 | 8 | 1
2 | Analogue Inputs (Duty) | 0 | 0 | 0 | 0 | 0
3 | Analogue Inputs (Standby) | 0 | 0 | 0 | 0 | 0 | 8 | 0
4 | Analogue Inputs (Assist) | 0 | 0 | 0 | 0 | 0
5 | Analogue Outputs (Normal) | 0 | 0 | 0 | 0 | 0 | 4 | 0
6 | Analogue Outputs (Duty) | 0 | 0 | 0 | 0 | 0
7 | Analogue Outputs (Standby) | 0 | 0 | 0 | 0 | 0 | 4 | 0
8 | Analogue Outputs (Assist) | 0 | 0 | 0 | 0 | 0
9 | Digital Inputs (Normal) | 19 | 18.75 | 6 | 0 | 25 | 16 | 2
10 | Digital Inputs (Duty) | 0 | 0 | 0 | 0 | 0
11 | Digital Inputs (Standby) | 0 | 0 | 0 | 0 | 0 | 16 | 0
12 | Digital Inputs (Assist) | 0 | 0 | 0 | 0 | 0
13 | Digital Outputs (Normal) | 3 | 81.25 | 13 | 0 | 16 | 16 | 1
14 | Digital Outputs (Duty) | 0 | 0 | 0 | 0 | 0
15 | Digital Outputs (Standby) | 0 | 0 | 0 | 0 | 0 | 16 | 0
16 | Digital Outputs (Assist) | 0 | 0 | 0 | 0 | 0
| Total | 23 | 53.0612 | 26 | 0 | 49 |  | 4
PLC Profibus signal count (Bytes)
| Intelligent I / O | Drive Duty Link | Drive Standby Link | Total Bytes
| Analogue Inputs | 55 | 0 | 55
| Analogue Outputs | 11 | 0 | 11
| Digital Inputs | 8 | 0 | 8
| Digital Outputs | 1 | 0 | 1
| Total | 75 | 0 | 75
| Input Memory Bytes Used | TBC | TBC | TBC
| Output Memory Bytes Used | TBC | TBC | TBC
Note:- 1. Profibus Signal Count should be Copied from the Soft I/O Template Count Summary sheet.
2. Links which are not used in the Project should be deleted.

## Sys Arch Overview
Project Title: United Utilities - Tyldesley UID PLC05 - Chemical Dosing
UUID: 80021608_02
Contract Title: System Integration
Document Title: Software Design Specification
SDS Annexure
SYSTEM ARCHITECTURE - OVERVIEW
| Legend |  | Description | Legend |  | Description |  | NOTE | - Ethernet Network configuration | NOTE…Contd
|  | PROFIBUS DP |  |  | MPI |  | Ref : 02 - 3rd Dec 2013 | Name Server Entry : PLC# X .Y (X=PLC no,Y=Site Name) |  | Note:1 -
|  | Profibus PA for Hazardous areas |  |  | RS232 |  |  | IP Address : 10.168.1.X (X = Ethernet node address (Node no)) |  | Note:2 -
|  | Profibus PA for Non - Hazardous areas |  |  | DH+ Electrical |  |  | Subnet Mask :255.255.255.0 ( Class C Subnet Mask) |  | Note:3 -
|  | Ethernet - Electrical |  |  | Existing System / Network |  |  | Default Gateway : 255.255.255.250 |  | Note:4 -
|  | DH 485 |  |  | New System / Network |  |  | NOTE | - Profibus Network configuration | Note:5 -
|  | Ethernet - Fibre Optic | [5 empty] | Baud Rate: 1500 K Baud |  | Note:6 -
IMS - Storm Water Pump 1 - P001
IMS - Storm Water Return Pump 1 - P101
UL FT - Storm Water Flow - FIT2001
MAG FT - Inlet Flow - FIT100
Quality Monitor QIT4001
Storm Tank 1 Level LT - LIT5001
Tank 1 Level LT - LIT5003
Flow - FIT2004

## Sys Arch Detailed
Project Title: United Utilities - Tyldesley UID PLC05 - Chemical Dosing
UUID: 80021608_02
Contract Title: System Integration
Document Title: Software Design Specification
SDS Annexure
SYSTEM ARCHITECTURE - DETAILED
Siemens PLC #05
Scalance X204-2
[10 empty] | Slot | 1 |  | 2 | 3 | 4 | 5 |  | 6 |  | 7 | 8 |  | 9 | 10 | 11
[10 empty] | Rack #0 | PS 307,5A 6ES7 307-1EA00-0AA0 |  | CPU-315-2PN/DP 6ES7 315-2EH14-0AB0 | IM360 6ES7 360-3AA01-0AA0 | SM-331, 8AI-N 6ES7 331-7KF02-0AB0 | SM-321, 16DI, 24V DC-N 6ES7 321-1BH02-0AA0 |  | SM-321, 16DI, 24V DC-N 6ES7 321-1BH02-0AA0 |  | SM-322, 16DO-N 6ES7 322-1HH01-0AA0 | SPARE |  | SPARE | SPARE | SPARE
HMI MP277
[10 empty] | Starting Address |  |  |  |  | PIW 128 | I 0.0 |  | I 2.0 |  | Q 0.0
T
[17 empty] | 11 |  | DIRIS-Incomer Multi-Function Power Meter | [6 empty] | DIRI0948v3.GSD
[17 empty] | 12 |  | PULSAR-A5-LIT315 Chemical Tank Lvl | [6 empty] | PULSE07E2.GSD
[17 empty] | 13 |  | PULSAR-A5-LIT323 Blind Tank Ultransonic Lvl | [6 empty] | PULSE07E2.GSD
[17 empty] | 14 |  | GRUNDFOS-A5-P504 Chemical Dosing Pump | [6 empty] | DME940.GSD | GRUN0971.GSD
| Legend |  | Description |  |  |  | Legend |  | Description | [12 empty] | NOTE | [5 empty] | NOTE…Contd
|  | PROFIBUS DP | [5 empty] | MPI | [13 empty] | Note:1 - | [5 empty] | Note:4 -
|  | Profibus PA for Hazardous areas | [5 empty] | RS232 | [13 empty] | Note:2 - RESERVE indicates that the position is reserved in software configuration and Physically there is "NO GAP" between modules. The modules are to be placed side by side. | [5 empty] | Note:5 -
|  | Profibus PA for Non - Hazardous areas | [5 empty] | DH+ Electrical | [19 empty] | Note:6 -
|  | Ethernet - Electrical | [5 empty] | Existing System / Network | [19 empty] | Note:7 -
|  | DH 485 | [5 empty] | New System / Network | [19 empty] | Note:8 -
|  | Ethernet - Fibre Optic | [5 empty] | PA Profibus Cable | [13 empty] | Note:3 - | [5 empty] | Note:9 -
To Telemetry
Dosing Control Panel - CP02

## PLC Power calculation
Project Title: United Utilities - Tyldesley UID PLC05 - Chemical Dosing
UUID: 80021608_02
Contract Title: System Integration
Document Title: Software Design Specification
SDS Annexure
PLC Power Requirement
Sr.No | Module Type | PART No. | Module VA | Quantity | Total KVA
1 | PS | PS307 5A | 550 | 1 | 0.55
2 | HMI | MP277 | 30.8571 | 1 | 0.030857
3 | Ethernet Switch | Scalance X204-2 | 20.5714 | 1 | 0.020571
Total KVA Requirement |  |  |  |  | 0.60143
Notes:
1) All module power consumption calculations are based on S7-300/S7-400 backplane bus (5Vdc).
2) Power calculation is based on Power factor = 0.7
2) This document shall be used by Alliance Contractor during panel engineering.

## PS Module selection
Project Title: United Utilities - Tyldesley UID PLC05 - Chemical Dosing
UUID: 80021608_02
Contract Title: System Integration
Document Title: Software Design Specification
SDS Annexure
Module placement & power supply selection based on module power consumption
S7-300 PLC #05 ( Chemical )
Rack No. | Module Type | Module Reference | Quantity | Module Current (mA) | Total current (Amp) | Module Size | Total Module Size
0 | CPU | CPU315 | 1 | 1000 | 1 | 40 | 40
| Interface Module | IM360 |  | 350 | 0 | 40 | 0
| Comm. Processor | CP341 | 0 | 200 | 0 | 40 | 0
| Comm. Processor | CP342 | 0 | 150 | 0 | 40 | 0
| Comm. Processor | CP343 | 0 | 200 | 0 | 80 | 0
| Analogue Input | SM331 | 1 | 60 | 0.06 | 40 | 40
| Analogue Output | SM332 | 0 | 60 | 0 | 40 | 0
| Digital Input | SM321 | 2 | 25 | 0.05 | 40 | 80
| Digital Output | SM322 | 1 | 100 | 0.1 | 40 | 40
| Total Current for the rack |  |  |  | 1.21
| Power supply module selected : 6ES7 307-1EA00-0AA0, 5 Amps |  | 1 |  |  | 80 | 80
| Total Module size for the rack selection | [5 empty] | 280
Notes:
1) All module power consumption calculations are based on S7-300/S7-400 backplane bus (5Vdc).
2) This document shall be used by Alliance Contractor during panel engineering.

## PLC Bill of Material
Project Title: United Utilities - Tyldesley UID PLC05 - Chemical Dosing
UUID: 80021608_02
Contract Title: System Integration
Document Title: Software Design Specification
SDS Annexure
PLC Bill Of Material (BOM)
Part Number | Description | Qty | Note
S7-300 System
PLC#1
S7-400 CPU for Medium / Large Systems
Large Systems / Remote Access Systems (Routing Functionality)
6ES7 414-2XK05-0AB0 | SIMATIC S7-400, CPU 414-2 CPU WITH: 1 MB WORKING MEMORY, (0,5 MB CODE, 0,5 MB DATA), 1. INTERFACE MPI/DP 12 MBIT/S, 2. INTERFACE PROFIBUS DP
6ES7 416-2XN05-0AB0 | SIMATIC S7-400, CPU 416-2 CPU WITH: 5.6 MB WORKING MEMORY, (2.8 MB CODE, 2.8 MB DATA), 1. INTERFACE MPI/DP 12 MBIT/S, 2. INTERFACE PROFIBUS DP To be used where a high memory requirement has been determined
6ES7 407-0DA02-0AA0 | S7-400, PS 407 4A, 120/230V AC
6ES7 407-0KA02-0AA0 | S7-400, PS 407 10A, 120/230V AC
6ES7 400-1JA01-0AA0 | SIMATIC S7-400, UR2 RACK, CENTRALIZED AND DISTRIBUTED WITH 9 SLOTS 2 REDUNDANT PS PLUGGABLE
6ES7 971-0BA00 | SIMATIC S7-400, BACK-UP BATTERY 3.6 V/1.9 AH FOR PS 405 4A/10A/20A AND PS 407 4A/10A/20A
6ES7 952-1KK00-0AA0 | SIMATIC S7, MEMORY CARD FOR S7-400, LONG VERSION, 5V FLASH-EPROM, 1 MBYTE
6ES7 952-1KL00-0AA0 | SIMATIC S7, MEMORY CARD FOR S7-400, LONG VERSION, 5V FLASH-EPROM, 2 MBYTES
6ES7 952-1KM00-0AA0 | SIMATIC S7, MEMORY CARD FOR S7-400, LONG VERSION, 5V FLASH-EPROM, 4 MBYTES
S7-300 CPU for Medium / Small Systems
Medium / Large Systems
6ES7 317-2AJ10-0AB0 | S7-317-2DP CPU. 512KB working memory - To be used where a high memory requirement has been determined or 4 Profibus DP networks are required.
6ES7 315-2AG10-0AB0 | S7-315-2DP CPU. 128KB working memory | 1
6ES7 307-1EA00-0AA0 | Simatic S7-300, Stabilized Power Supply, Ps 307, 120/230 V AC; 24 V DC, 5 A | 1
6ES7 953-8LG20-0AA0 | MMC 128Kb for S7-300
6ES7 953-8LJ20-0AA0 | MMC 512Kb for S7-300/ET200S IM151
6ES7 953-8LL20-0AA0 | MMC 2Mb for S7-300/ET200S IM151 | 1
6ES7 953-8LM20-0AA0 | MMC 4Mb for S7-300/ET200S IM 151
6ES7 953-8LP20-0AA0 | MMC 8Mb for S7-300/ET200S IM 151
Small Systems
6ES7 313-6CF03-0AB0 | 313C-2DP 16/16D 3 Cntr 30Khz 64Kb
6ES7 307-1BA00-0AA0 | Simatic S7-300, Stabilized Power Supply, Ps 307, 120/230 V AC; 24 V DC, 2 A
6ES7 953-8LF20-0AA0 | MMC 64Kb for S7-300/ET200S IM151
6ES7 392-1AM00-0AA0 | Simatic S7-300, Front Connector 392 With Screw Contacts, 40-Pin
DCS Systems
6ES7 65xxx | Simatic PCS7 DCS controller using standard Simatic S7300/400 I/O & comms - Refer to Siemens applications team
I/O Racks / Modules
6ES7 390-1AB60-0AA0 | Simatic S7-300, Rail L=160mm
6ES7 390-1AE80-0AA0 | Simatic S7-300, Rail L=480mm
6ES7 390-1AF30-0AA0 | Simatic S7-300, Rail L=530mm | 1
6ES7 390-1AJ30-0AA0 | Simatic S7-300, Rail L=830mm
6ES7 390-1BC00-0AA0 | Simatic S7-300, Rail L=2000mm
6ES7 360-3AA01-0AA0 | Simatic S7-300,Interface Module IM 360 In Central Rack For Connecting Max. 3 Expansion Racks
6ES7 361-3CA01-0AA0 | Simatic S7-300,Interface Module IM 361 In Expansion Rack For Connecting To Central Rack (IM 360),24 V DC Supply Voltage
6ES7 368-3BB01-0AA0 | SIMATIC S7-300,CONNECTING CABLE BETWEEN IM 360/IM 361 1M
6ES7 153-2BA02-0XB0 | SIMATIC DP, IM153-2 HIGH FEATURE W. INTEGRATED PROFIBUS
6ES7 321-1BH02-0AA0 | SM321, 16 x Dig in, 24 V DC | 2
6ES7 322-1BH01-0AA0 | SM322, 16 x Dig out, 24 V DC, 0.5A | 1
6ES7 322-1HH01-0AA0 | SM322, 16 x Dig out, (Relay)
6ES7 331-7KF02-0AB0 | SM331; 8 x An in; 9/12/14 bit res. | 1
6ES7 331-7KB02-0AB0 | SM331; 2 x An in; 9/12/14 bit res.
6ES7 332-5HD01-0AB0 | SM332; 4 x An out U/I; Diagnostics; Resolution 11/12bits
6ES7 332-5HB01-0AB0 | SM332; 2 x An out; 11/12 bit res.
6ES7 392-1AJ00-0AA0 | S7-300 Front Connector, screw, 20-Pin | 4
HMI
6AV6 642-0BA01-1AX0 | TOUCH PANEL TP177B 5:7" 256 COLOUR with Profibus DP + Ethernet
6AV6 643-0CD01-1AX0 | MP277 10" TFT Display Touch | 1
6AV6 644-0AA01-2AX0 | MP377 12" Touch
6AV6 545-0DA10-0AX0 | MP370 - 12" COLOUR TFT DISPLAY - TOUCH
6AV6 645-0AA01-0AX0 | SIMATIC MOBILE PANEL 177 DP WITH INTEGRATED ENABLING BUTTON
6AV6 671-5AE00-0AX0 | CONNECTIVITY BOX DP BASIC FOR MOBILE PANELS (MPI/PROFIBUS)
6AV6 574-1AF04-4AA0 | MOBILE PANEL WALL MOUNTING
6XV1 440-4AH20 | MOBILE PANEL 2 MTS CABLE
6AV6671-8XB10-0AX1 | SD Card 512MB | 1
6AV6 671-1CB00-0AX1 | MultiMedia Card 64MB - for TP177 & Mobile 177 only
6AV6 574-2AC00-2AA1 | CF Card, 512 MB
Compact Remote I/O
6ES5 710-8MA11 | M-BLOCK 483MM SPECIAL RAIL
6ES5 710-8MA21 | M-BLOCK 530MM SPECIAL RAIL
6ES5 710-8MA31 | M-BLOCK 830MM SPECIAL RAIL
6ES5 710-8MA41 | M-BLOCK 2000MM SPECIAL RAIL
6ES7 151-1BA02-0AB0 | ET200S INTERFACE MODULE HIGH FEATURE
6ES7 138-4CA01-0AA0 | SIMATIC DP POWER MODULE PME
6ES7 193-4CE00-0AA0 | SIMATIC DP, TERMINAL MODULE TM-P15S22-01 FOR ET 200S FOR POWER MODULES 15 MM WIDE,SCREW-TYPE TERMINALS 2X2 TERMINAL CONNECTIONS W/O TERMINAL LEAD TO AUX1 AUX1 IN LINE
6ES7 131-4BD01-0AA0 | SIMATIC DP, 5 electronic modules for ET200S, 4 x Dig input Std. 24V DC, 15mm width, 5 off per pack
6ES7 132-4BD01-0AA0 | SIMATIC DP, 5 electronic modules for ET200S, 4 x Dig output Std. 24V DC, 15mm width, 5 off per pack
6ES7 132-4HB01-0AB0 | SIMATIC DP, 5 ELECTRON. MODULES FOR ET 200S, 2 DO RELAY 24V DC - 230V AC/5A,15 MM WIDTH FIRST-UP SIGNAL WITH LED SF (GROUP FAULT), 5 PER PACKAGING UNIT
6ES7 134-4GB01-0AB0 | SIMATIC DP, ELECTRONIC MODULE FOR ET 200S, 2 AI STAND. I-2DMU 15 MM WIDE +/-20MA; 13 BIT + SIGN, 4 .. 20MA; 12 BIT FOR 2-WIRE TRANSDUCER CYCLE TIME 65 MS/CHANNEL WITH LED SF (GROUP FAULT)
6ES7 134-4GB11-0AB0 | SIMATIC DP, ELECTRONIC MODULE FOR ET 200S, 2 AI STAND. I-4DMU 15 MM WIDE +/-20MA; 13 BIT + SIGN, 4 .. 20MA; 12 BIT FOR 4-WIRE TRANSDUCER CYCLE TIME 65 MS/CHANNEL WITH LED SF (GROUP FAULT)
6ES7 135-4GB01-0AB0 | SIMATIC DP, ELECTRONIC MODULE FOR ET 200S, 2 AO I 15 MM WIDE, +/-20MA; 13 BIT + SIGN, 4 . .20MA; 12 BIT CYCLE TIME < 1 MS WITH LED SF (GROUP FAULT)
6ES7 193-4CB20-0AA0 | SIMATIC DP, 5 TERMINAL MODULES TM-E15S24-01 FOR ET 200S FOR ELECTRONIC MODULES 15MM WIDE, SCREW-TYPE TERMINALS 2X4 TERMINAL CONNECTIONS W/O TERMINAL LEAD TO AUX1 AUX1 IN LINE, 5 UNITS PER PACK.
6ES7 193-4GA00-0AA0 | 5 SHIELD CONNECTING ELEMENTS TERMINAL MODULES TM-P AND TM-E THE ET 200S AS RETAINING DEVICE FOR POWER RAIL 3 X 10 MM F. CONNECTION OF SHIELDED LEADS
6ES7 193-4GB00-0AA0 | 5 TERMINAL ELEMENTS F. ET 200S F.CONNECTION OF BRAIDED SHIELDS WITH THE POWER RAIL
8WA2 842 | N BUSBAR, TIN PLATED CU 10X3MM, 1M
8WA2 868 | L-SIDE TERM <25MM2 F.10X3MM N-BBAR
Communications
6GK7 343-1EX30-0XE0 | SIMATIC NET CP 343-1 Ind Eth f. S7-300
6GK7 343-1CX10-0XE0 | SIMATIC NET, CP 343-1 LEAN COMMUNICATIONS PROCESSOR
6GK7 342-5DA02-0XE0 | SIMATIC NET, CP 342-5 COMMUNICATIONS PROCESSOR FOR ELECTRICAL CONNECTION OF SIMATIC S7-300 TO PROFIBUS UP TO 12 MBAUD
6ES7 341-1AH01-0AE0 | Simatic S7-300, CP341 Communication Processor With RS232C Interface (V.24)
6ES7 870-1AB01-0YA0 | CP341/441-2 Modbus Slave V3.1
6GK7 443-1EX11-0XE0 | SIMATIC NET, CP 443-1 COMMUNICATIONS PROCESSOR FOR CONNECTION OF A SIMATIC S7-400 W. IND.ETHERNET VIA TCP/IP AND ISO, S7 COMM., FETCH / WRITE, SEND/RECEIVE W. OR WITHOUT RFC
6GK7 443-5DX04-0XE0 | SIMATIC NET, CP 443-5 EXTENDED COMMUNICATIONS PROCESSOR FOR CONNECTING SIMATIC S7-400 TO PROFIBUS, REQUIRES: STEP7 V5.X
WAN communications (refer to Siemens for detailed design)
SINUAT S7 WAN system - Refer to Siemens applications team
Programming Device
6ES7 713-1BB11-0AA0 | SIMATIC FIELD PG M2 PREMIUM 2,2 GHZ CORE 2 DUO (T7500), DL MULTISTANDARD DVD RW, 15" SXGA+ DISPLAY (1400 X 1050) 160GB S-ATA HDD, 1X2GB DDR2 RAM POWER CABLE FOR: UNITED KINGDOM; WLAN APPROVAL: 2,4GHZ F. EUROPE 5GHZ F. GE, FR, IT, SP, UK, AT, MODEM APPROVAL FOR EUROPE; WINDOWS XPPROF ENGLISH MUI WITH GE/FR/SP/IT ON HDD AS IMAGE; TRIAL LICENSE FOR STEP7 PROF AND WINCC FLEXIBLE ADV.; VERSION OF SOFTWARE 10/2007
6ES7 712-1BB11-0AD5 | Field PG M Premium2 GHz Pentium M (760) DL Multistandard DVD RW; 15" SXGA+ Display (1400x2950) 80 Gbyte S-ATA Harddrive 2 x 512 MB DDR2 RAM AC-plug and keyboard; United Kingdom Win XP MUI (French, Spanish, Italian, German, English, etc.) Licence STEP 7; STEP 7-Micro/WIN; WinCC Flex Adv. Version of SIMATIC Software; Edition 09/2006 ( STEP 7 V5.4); STEP 7-Micro/WIN V 4.0.2; STEP 5 V7.23 HF1;WinCC Flex adv.
6ES7713-1BB11-0AD0 | SIMATIC FIELD PG M2 PREMIUM 2,2 GHZ CORE 2 DUO (T7500), DL MULTISTANDARD DVD RW, 15" SXGA+ DISPLAY (1400 X 1050) 160GB S-ATA HDD, 1X2GB DDR2 RAM POWER CABLE FOR: UNITED KINGDOM; WLAN APPROVAL: 2,4GHZ F. EUROPE 5GHZ F. GE, FR, IT, SP, UK, AT, MODEM APPROVAL FOR EUROPE; WINDOWS XPPROF ENGLISH MUI WITH GE/FR/SP/IT ON HDD AS IMAGE; LICENSE FOR STEP7 PROF, STEP5, STEP7 MICROWIN AND WINCC FLEXIBLE ADV.; INCL. EPROM ADAPTER AND S5-PLC CABLE; VERSION OF SOFTWARE 10/2007
PLC Software
6ES7 810-4CC08-0YA5 | STEP 7 Version 5.4
6ES7 972-0CB20-0XA0 | SIMATIC S7, USB PC ADAPTER
6ES7 901-1BF00-0XA0 | Simatic S7, Connecting Cable For Hmi Adapter And PC/TS Adapter 5 M
6ES7 810-4BC01-0YX2 | STEP7 Software update Service (SUS) annual contract
HMI Software
6AV6 612-0AA51-2CA5 | WinCC Flexible Standard 2007
6AV6 618-7AB01-2AB0 | WINCC FLEXIBLE /SM@RTACCESS FOR SIMATIC PANEL RUNTIME SW, SINGLE LICENSE, LICENSE KEY ON USB STICK, TO BE USED WITH SIMATIC PANEL 177B/270/370 SERIES, (FOR VERSION 2007)
6AV6 618-7BB01-2AB0 | WINCC FLEXIBLE /SM@RTSERVICE FOR SIMATIC PANEL RUNTIME SW, SINGLE LICENSE LICENSE KEY ON USB STICK TO BE USED WITH SIMATIC PANEL 177B/270/370 SERIES (FOR VERSION 2007) | 1
6AV6 612-0AA00-0AL0 | SUS for WinCC flexible Standard
SCADA Software
6AV6 381-1BQ06-2AX0 | SIMATIC WinCC V6.2 RC64k Tag
6AV6 381-1AA00-0AX5 | WINCC COMPREHENSIVE SUPPORT FOR 12 MONTHS
6AV6371-1DH06-2AX0 | WinCC V6.2 Web Navigator 3 Client
6AV6371-1DH06-2BX0 | WinCC V6.2 Web Navigator 10 Client
6AV6371-1DH06-2CX0 | WinCC V6.2 Web Navigator 25 Client
6AV6371-1DH06-2DX0 | WinCC V6.2 Web Navigator 50 Client
6AV6371-1DN06-2AX0 | WinCC Dat@Monitor V6.2 SP2 3 clients
6AV6371-1DN06-2BX0 | WinCC Dat@Monitor V6.2 SP2 10 clients
6AV6 371-1DN06-2CX0 | WinCC Dat@Monitor V6.2 SP2 25 clients
6AV6 371-1DN06-2DX0 | WinCC Dat@Monitor V6.2 SP2 50 clients
SCADA Workstation
GB3:UUSCADAkit1 | PC547B Bundle includes: PC, Tower Kit, Diagmonitor, 19" TFT Monitor, Keyboard, Mouse, HP Laserjet 2605 and UPS Module 1KVA + External Bypass + Ethernet
GB3:UUSCADAkit2 | PC547B Bundle includes: PC, Tower Kit, Diagmonitor, 19" TFT Monitor, Keyboard, Mouse and HP Laserjet 2605
GB3:UUSCADAkit3 | PC547B Bundle includes: PC, Tower Kit, Diagmonitor, 19" TFT Monitor, Keyboard and Mouse
6AG4 104-0CC23-0BX0 | SIMATIC RACK PC 547B, INTERFACES: 1X GBIT LAN (RJ45); 1X SERIAL (COM1); 1X PARALLEL (LPT); 4X USB 2X USB FRONT SIDE 2XPS/2; AUDIO; 7 SLOTS (4X PCI LONG, 1X PCIE X 16, 2X PCIE X 1); DRIVE BAYS: 6 (3X5,25", 1X3,5" FRONT-ACCESS; 2X3,5" INTERNAL); TEMPERATURE AND FAN CONTROL WATCHDOG; BOARD RETAINER; CORE 2 DUO E4300 (1.8 GHZ, 800 MHZ FSB, 2MB L2 CACHE, EM64-T) RAID1 (2X250 GBYTE HDD SATA, MIRROR DIKS); INTERNAL 2.0 GBYTE DDR2 SDRAM (2 X 1.0GB), DUAL CHANNEL DVD-ROM & FDD; WITHOUT EXPANSIONS WINDOWS XP PROF. MULTI-LANG. (EN, DE, FR, IT, SP), SP2 WITHOUT SOFTWARE; 110/230V INDUSTR. POWER SUPPLY; POWER SUPPLY CORD EUROPE;
6SU1062-2AA00 + EMBS1013 + AKMUN2M | UPS Module A1000 1KVA + external bypass switch + SNMP adapter (Ethernet)
Profibus
6ES7 658-3LX06-0YA5 | SIMATIC PDM, SOFTWARE PCS 7 V6.0 (128 TAGS)
6ES7 972-0BB50-0XA0 | SIMATIC S5/S7,BUS CONNECTOR FOR PROFIBUS UP TO 12 MBIT/S 90 DEGREE ANGLE OUTGOING CABLE, (WX H X D): 16 X 72,7 X 34 MM IPCD TECHOLOGY FAST CONNECT, WITH PG SOCKET | 1
6GK1 500-0FC00 | Simatic Net, RS485 Bus Connector IPC/OP
6GK1 905-6AA00 | Simatic Net, Profibus Fast Connect StriPPIng Tool, Tool For Fast StriPPIng Of The Profibus Fast Connect Bus Cable
6XV1 830-0EH10 | Simatic Net, Profibus Fast Connect Standard Bus Cable 2 Cores, Shielded, Special Design F. Fast Mounting Consignment: Max. Available Length: 1000 M, Minim. Ordering Quant.: 20 M, Sold By The Meter
6XV1 830-3FH10 | PROFIBUS FC UNDERGROUND CABLE, £/M
6ES7 972-0AA01-0XA0 | SIMATIC S7, RS485 REPEATER
6ES7 972-0AB01-0XA0 | DIAGNOSTIC REPEATER FOR PROFIBUS DP
6ES7 181-0AA01-0AA0 | BT200 Bus test unit for Profibus Ver 2
6ES7 193-8LA00-0AA0 | Charger for Ver 2 BT200 or higher
6ES7 193-8MA00-0AA0 | Protocol kit for BT200
6GK1 503-3CB00 | PROFIBUS OLM/G12 W. RS485 + FO I/FS V4.0 (replaces V3.1)
6XV1 820-5BH10 | Simatic Net, Fiber Optic Cable Standard Cable, with 4 BFOC Connectors, 1 M
6XV1 820-5BH20 | Simatic Net, Fiber Optic Cable Standard Cable, with 4 BFOC Connectors, 2 M
6XV1 820-5BH50 | Simatic Net, Fiber Optic Cable Standard Cable, with 4 BFOC Connectors, 5 M
6XV1 820-5BN10 | Simatic Net, Fiber Optic Cable Standard Cable, with 4 BFOC Connectors, 10 M
6XV1 820-5BN15 | Simatic Net, Fiber Optic Cable Standard Cable, with 4 BFOC Connectors, 15 M
6XV1 820-5BN20 | Simatic Net, Fiber Optic Cable Standard Cable, with 4 BFOC Connectors, 20 M
6XV1 820-5BN30 | Simatic Net, Fiber Optic Cable Standard Cable, with 4 BFOC Connectors, 30 M
6XV1 820-5BN50 | Simatic Net, Fiber Optic Cable Standard Cable, with 4 BFOC Connectors, 50 M
6XV1 820-5BN75 | Simatic Net, Fiber Optic Cable Standard Cable, with 4 BFOC Connectors, 75 M
6XV1 820-5BT10 | Simatic Net, Fiber Optic Cable Standard Cable, with 4 BFOC Connectors, 100 M
6XV1 820-5BT20 | Simatic Net, Fiber Optic Cable Standard Cable, with 4 BFOC Connectors, 200 M
6GK1 503-3CA00 | PROFIBUS OLM/P12, 1XRS485, 2XPLASTIC V4.0 (replaces V3.1)
6XV1 821-0AH10 | PLASTIC FO CABLE £ PER M MIN 20M MAX 1KM
0 | 0
6ES7 972-0DA00-0AA0 | Active RS485 Terminating element | 1
6ES7 158-0AD01-0XA0 | Simatic DP, Distributed I/O DP/DP Coupler Coupling Module For Connecting Two Profibus DP Networks
6GK1 561-3AA01 | SIMATIC NET, CP 5613, PCI CARD FOR CONNECTION W. PROFIBUS-DP, WINDOWS 2000PRO/SV, XP PRO
6GK1 713-5CB64-3AA0 | Profibus-S7-5613/Win V6.3, 2006 CD
SST-PFB-SLC | Profibus Card for Allen-Bradley SLC range PLC
SST-PFB-CLX | Profibus Card for Allen-Bradley Contrologix range PLC
Profibus PA
6GK1 905-0AA00 | SPLITCONNECT TAP PACK OF 10
6GK1 905-0AB10 | PROFIBUS PA SPLITCONNECT M12 OUTLET PACK OF 5
6GK1 905-0AD00 | SIMATIC NET, PROFIBUS PA SPLITCONNECT TERMINATOR (EX) PK OF 5
6GK1 905-0AE00 | SIMATIC NET, PROFIBUS PA SPLITCONNECT TERMINATOR (NON-EX) PK OF 5
6GK1 905-0AF00 | SIMATIC NET, PB PA SPLITCONNECT M12 JACK, CONNECT PACK OF 5
6XV1 830-5EH10 | PROFIBUS PA CABLE, FC, IEC 1158-2 BLUE FOR Ex APPLICATIONS
6XV1 830-5FH10 | PB FC BUS CABLE FOR IEC 61158-2 BLACK FOR NON-Ex APPLICATIONS
6ES7 157-0AD82-0XA0 | DP/PA COUPLER EX (IA) 110MA
6ES7 157-0AC83-0XA0 | DP/PA COUPLER, NON EX, EXPANDED TEMP VER -
Please note: DP/PA LINK; a link module should always be used in conjunction with a coupler to achieve a true DP/PA LINK.
6ES7 153-2BA81-0XB0 | IM153-2 Interface for DP/PA link and Y link MODULE DPV1 SLAVE - Used with coupler to create link module
Ethernet
6GK5 204-2BB10-2AA3 | SIMATIC NET SCALANCE X204-2 | 1
6GK5 208-0BA10-2AA3 | SIMATIC NET SCALANCE X208
6GK5 202-2BB00-2BA3 | SIMATIC NET SCALANCE X202-2IRT with Redundancy Manager
6GK5 204-0BA00-2BA3 | SIMATIC NET SCALANCE X204-IRT with Redundancy Manager
6GK1 900-0AB00 | SIMATIC NET, C- PLUG
6GK1 105-2AE00 | SIMATIC NET, OSM TP22, 2 RJ45, 4DI
6GK1 105-2AB10 | OSM TP62 IND ETH, 2FO + 6 RJ45 PORTS
6GK1 105-3AB10 | ESM TP80 IND ETH, 8 RJ45 PORTS 10/10
6GK1 161-3AA01 | SIMATIC NET, IE, CP 1613 A2 PCI CARD (32BIT; 33MHZ/66MHZ; 3.3V/5V UNIVERSAL KEY) FOR CONNECTION TO IND. ETHERNET (10/100MBIT/S) WITH ITP AND RJ 45 PORT VIA S7-1613 AND S7-REDCONNECT. INCL. DRIVER F. MS WINDOWS (32BIT), 2000PRO/SERVER, XP PRO, 2003 SERVER
6XV1 840-2AH10 | SIMATIC NET, IE FC TP STANDARD CABLE, TP INSTALLATION CABLE FOR CONNECTION TO FC OUTLET RJ45, FOR UNIVERSAL APPLICATION, 4-WIRE, SHIELDED, CAT. 5, SOLD BY THE METER MAX. CONSIGNMENT: 1000 M, MIN. ORDERING QUANTITY: 20 M
6GK1 901-1GA00 | SIMATIC NET,INDUSTRIAL ETHERNET FASTCONNECT STRIPPING TOOL, FOR RAPID STRIPPING OF INDUST. ETHERNET FASTCONNECT CABLES
6GK1 901-1FC00-0AA0 | SIMATIC NET, IE FC OUTLET RJ45 INDUSTRIAL ETHERNET FASTCONNECT OUTLET RJ45 F. TRANSITION FROM IE FC CABLES AND TP CORD PATCH CABLES
6GK1 901-1BB10-2AA0 | SIMATIC NET IE FC RJ45 PLUG 180 RJ45 PLUG CONNECTOR W. RUGGED METAL HOUSING AND FC CONNECTING METHOD, 180 DGR CABLE OUTLET 1 PACK = 1 PCS
6XV1 850-2GH10 | SIMATIC NET, IND. ETHERNET TP CORD RJ45/RJ45, TP CORD PREASSEMBLED WITH 2 RJ45 CONNECTORS, LENGTH 1 M
6XV1 850-2GH20 | SIMATIC NET, IND. ETHERNET TP CORD RJ45/RJ45, TP CORD PREASSEMBLED WITH 2 RJ45 CONNECTORS, LENGTH 2 M
6XV1 850-2GH60 | SIMATIC NET, IND. ETHERNET TP CORD RJ45/RJ45, TP CORD PREASSEMBLED WITH 2 RJ45 CONNECTORS, LENGTH: 6 M
6GK1 716-1CB64-3AA0 | Ind Ethernet S7-1613/Win V2006 CD
Scalance W Wireless Modules - refer to UU EICA Category Manager
Sitop Power Supplies
6EP1 331-2BA10 | SITOP POWER 0.5A 93-264VAC IN
6EP1 333-3BA00 | SITOP MODULAR PSU 120/230VAC, 24VDC 5A
6EP1 334-3BA00 | SITOP3 1 OR 2 PHASE, 24VDC, 10A PFC
6EP1 336-3BA00 | SITOP3 1 PHASE, 24VDC, 20A PFC
6EP1 931-2DC21 | SITOP DC UPS MODULE 24 V/6 A, W/O INTERFACE INPUT: 24 V DC/6.85 A OUTPUT: 24 V DC/6 A
6EP1 935-6MD11 | SITOP POWER BATTERY MODULE 24 V/3.2 AH WITH SERVICE- FREE SEALED LEAD-ACID BATTERIES FOR DC-USV-MODULE 6 UND 15 SITOP POWER DC UPS MODULE 15
Backup Control Systems
6ED1 052-1HB00-0BA5 | LOGO! 24RC (6TH GENERATION)
6ED1 055-1HB00-0BA0 | LOGO! DM8 4DI 24V 4DQ RELAY
Maintenance Support Only
This section has been deleted - please refer to the A&D Mall or customer services for pricing

## PLC#05 Hardwired IO Count
Project Title: United Utilities - Tyldesley UID PLC05 - Chemical Dosing
UUID: 80021608_02
Contract Title: System Integration
Document Title: Software Design Specification
SDS Annexure
Hardwired I / O Database
Signal Hardwired Position in PLC |  |  | PLC Address | Type | PLC Tag | Description | State 0 | State 1 | Range | Engg. Unit | Reference Document Number | Document Description | Doc. Rev. | Process Unit | Instrument Tag as shown on P&ID | Instrument/Valve/Drive Type as per DS | Signal type | Remarks
Rack | Slot | Channel | [16 empty] | Norm N, Duty D, Standby S, Assist A | Used / Spare | DI | D0 | AI | AO | Norm DI Used | Norm DI Spare | Norm DO Used | Norm DO Spare | Norm AI Used | Norm AI Spare | Norm AO Used | Norm AO Spare | Dty DI Used | Dty DI Spare | Dty DO Used | Dty DO Spare | Dty AI Used | Dty AI Spare | Dty AO Used | Dty AO Spare | S/B DI Used | S/B DI Spare | S/B DO Used | S/B DO Spare | S/B AI Used | S/B AI Spare | S/B AO Used | S/B AO Spare | Ast DI Used | Ast DI Spare | Ast DO Used | Ast DO Spare | Ast AI Used | Ast AI Spare | Ast AO Used | Ast AO Spare
Analogue Inputs
0 | 4 | 0 | PIW 128 | AI | A5_FIT112_PV | Chemical Delivery Pump Flow | - | - | 0-625 | l/hr | WIG0179/80021608/01/13/71005 | FDS | A1 | Chemical | A5_FIT112 |  | AI |  | N | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 4 | 1 | PIW 130 | AI | SPARE_258 | Spare | - | - | - | - | - | - | - | - | - |  |  |  | N | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 4 | 2 | PIW 132 | AI | SPARE_260 | Spare | - | - | - | - | - | - | - | - | - |  |  |  | N | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 4 | 3 | PIW 134 | AI | SPARE_262 | Spare | - | - | - | - | - | - | - | - | - |  |  |  | N | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 4 | 4 | PIW 136 | AI | SPARE_264 | Spare | - | - | - | - | - | - | - | - | - |  |  |  | N | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 4 | 5 | PIW 138 | AI | SPARE_266 | Spare | - | - | - | - | - | - | - | - | - |  |  |  | N | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 4 | 6 | PIW 140 | AI | SPARE_268 | Spare | - | - | - | - | - | - | - | - | - |  |  |  | N | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 4 | 7 | PIW 142 | AI | SPARE_270 | Spare | - | - | - | - | - | - | - | - | - |  |  |  | N | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Digital Input Card 1 | [19 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 5 | 0 | I 0.0 | DI | CHEMDOSE_Mains | Chemical Dosing Main Supply Healthy | Fail | Healthy | - | - | WIG0179/80021608/01/13/71005 | FDS | A1 | Chemical | - | - | DI |  | N | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 5 | 1 | I 0.1 | DI | CHEMDOSE_110v | Chemical Dosing 110V Supply Healthy | Fail | Healthy | - | - | WIG0179/80021608/01/13/71005 | FDS | A1 | Chemical | - | - | DI |  | N | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 5 | 2 | I 0.2 | DI | CHEMDOSE_24A | Chemical Dosing 24V Supply A Healthy | Fail | Healthy | - | - | WIG0179/80021608/01/13/71005 | FDS | A1 | Chemical | - | - | DI |  | N | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 5 | 3 | I 0.3 | DI | CHEMDOSE_24B | Chemical Dosing 24V Supply B Healthy | Fail | Healthy | - | - | WIG0179/80021608/01/13/71005 | FDS | A1 | Chemical | - | - | DI |  | N | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 5 | 4 | I 0.4 | DI | A5_AV508_OPENED | Chemical Tank Outlet Valve | - | Opened | - | - | WIG0179/80021608/01/13/71005 | FDS | A1 | Chemical | A5_AV508 | - | DI |  | N | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 5 | 5 | I 0.5 | DI | A5_AV508_CLOSED | Chemical Tank Outlet Valve | - | Closed | - | - | WIG0179/80021608/01/13/71005 | FDS | A1 | Chemical | A5_AV508 | - | DI |  | N | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 5 | 6 | I 0.6 | DI | A5_AV508_MA | Chemical Tank Outlet Valve | - | Available | - | - | WIG0179/80021608/01/13/71005 | FDS | A1 | Chemical | A5_AV508 | - | DI |  | N | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 5 | 7 | I 0.7 | DI | A5_FIT112_HLTH | Chemical Dosing Pump flowmeter health | Fail | Healthy | - | - | WIG0179/80021608/01/13/71005 | FDS | A1 | Chemical | A5_FIT112 | - | DI |  | N | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 5 | 8 | I 1.0 | DI | A5_LS316 | Chemical Tank High High Level Switch | High High | Not High High | - | - | WIG0179/80021608/01/13/71005 | FDS | A1 | Chemical | A5_LS316 | - | DI |  | N | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 5 | 9 | I 1.1 | DI | A5_LS317 | Chemical Tank High Level Switch | High | Not High | - | - | WIG0179/80021608/01/13/71005 | FDS | A1 | Chemical | A5_LS317 | - | DI |  | N | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 5 | 10 | I 1.2 | DI | A5_LS318 | Chemical Catch Pot Level Switch | High | Healthy | - | - | WIG0179/80021608/01/13/71005 | FDS | A1 | Chemical | A5_LS318 | - | DI |  | N | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 5 | 11 | I 1.3 | DI | A5_LS319 | Chemical Dosing Skid | High | Healthy | - | - | WIG0179/80021608/01/13/71005 | FDS | A1 | Chemical | A5_LS319 | - | DI |  | N | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 5 | 12 | I 1.4 | DI | A5_LS320 | Chemical Dosing Line Catch Pot Level Switch | High | Healthy | - | - | WIG0179/80021608/01/13/71005 | FDS | A1 | Chemical | A5_LS320 | - | DI |  | N | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 5 | 13 | I 1.5 | DI | SPARE_5_13 | Spare | - | - | - | - | - | - | - | - | - | - |  |  | N | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 5 | 14 | I 1.6 | DI | SPARE_5_14 | Spare | - | - | - | - | - | - | - | - | - | - |  |  | N | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 5 | 15 | I 1.7 | DI | SPARE_5_15 | Spare | - | - | - | - | - | - | - | - | - | - |  |  | N | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Digital Input Card 2 | [19 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 6 | 0 | I 2.0 | DI | A5_LS321 | Chemical Dosing Dual Catch Pot Enclosure Level Sw | High | Healthy | - | - | WIG0179/80021608/01/13/71005 | FDS | A1 | Chemical | A5_LS321 | - | DI |  | N | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 6 | 1 | I 2.1 | DI | A5_LS322 | Emergency Shower Low Level Switch | Low | Healthy | - | - | WIG0179/80021608/01/13/71005 | FDS | A1 | Chemical | A5_LS322 | - | DI |  | N | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 6 | 2 | I 2.2 | DI | A5_LS324 | Chemical Blind Tank High High Level Switch | High High | Healthy | - | - | WIG0179/80021608/01/13/71005 | FDS | A1 | Chemical | A5_LS324 | - | DI |  | N | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 6 | 3 | I 2.3 | DI | A5_XS201 | Emergency Eyewash station 1 - Dosing Skid | Operated | Healthy | - | - | WIG0179/80021608/01/13/71005 | FDS | A1 | Chemical | A5_XS201 | - | DI |  | N | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 6 | 4 | I 2.4 | DI | A5_XS202 | Emergency Eyewash station 2 - Delivery Station | Operated | Healthy | - | - | WIG0179/80021608/01/13/71005 | FDS | A1 | Chemical | A5_XS202 | - | DI |  | N | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 6 | 5 | I 2.5 | DI | A5_XS203 | Emergency Shower | Operated | Healthy | - | - | WIG0179/80021608/01/13/71005 | FDS | A1 | Chemical | A5_XS203 | - | DI |  | N | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 6 | 6 | I 2.6 | DI | A5_TS601 | Emergency Header Tank Not Low Temperature | Low Temp | Healthy | - | - | - | - | - | - | - | - | - |  | N | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 6 | 7 | I 2.7 | DI | SPARE_6_7 | Spare | - | - | - | - | - | - | - | - | - | - | - |  | N | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 6 | 8 | I 3.0 | DI | SPARE_6_8 | Spare | - | - | - | - | - | - | - | - | - | - | - |  | N | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 6 | 9 | I 3.1 | DI | SPARE_6_9 | Spare | - | - | - | - | - | - | - | - | - | - | - |  | N | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 6 | 10 | I 3.2 | DI | UPS_Batt_Hlthy | Battery charger Healthy | Fail | Healthy | - | - | WIG0179/80021608/01/13/71005 | FDS | A1 | Chemical | - | - | - |  | N | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 6 | 11 | I 3.3 | DI | UPS_Changeover | A change-over test facility shall be provided | Fail | Healthy | - | - | WIG0179/80021608/01/13/71005 | FDS | A1 | Chemical | - | - | - |  | N | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 6 | 12 | I 3.4 | DI | UPS_Hlthy | UPS system healthy | Fail | Healthy | - | - | WIG0179/80021608/01/13/71005 | FDS | A1 | Chemical | - | - | - |  | N | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 6 | 13 | I 3.5 | DI | UPS_Low_Volts | Low volts signal healthy | Low | Healthy | - | - | WIG0179/80021608/01/13/71005 | FDS | A1 | Chemical | - | - | - |  | N | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 6 | 14 | I 3.6 | DI | UPS_Bypass | System in by-pass not in By-pass | Bypass | Not Bypass | - | - | WIG0179/80021608/01/13/71005 | FDS | A1 | Chemical | - | - | - |  | N | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 6 | 15 | I 3.7 | DI | Watchdog_Hlthy | Watchdog Healthy | Unhealthy | Healthy | - | - | WIG0179/80021608/01/13/71005 | FDS | A1 | Chemical | - | - | - |  | N | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Digital Output | [19 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 7 | 0 | Q 0.0 | DO | A5_AV508_OPENCMD | Chemical Tank Outlet Valve | - | OPEN | - | - | WIG0179/80021608/01/13/71005 | FDS | A1 | Chemical | A5_AV508 | - | DO |  | N | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 7 | 1 | Q 0.1 | DO | A5_AV508_CLOSECMD | Chemical Tank Outlet Valve | - | CLOSE | - | - | WIG0179/80021608/01/13/71005 | FDS | A1 | Chemical | A5_AV508 | - | DO |  | N | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 7 | 2 | Q 0.2 | DO | SPARE_7_2 | Spare | - | - | - | - | - | - | - | - | - | - |  |  | N | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 7 | 3 | Q 0.3 | DO | SPARE_7_3 | Spare | - | - | - | - | - | - | - | - | - | - |  |  | N | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 7 | 4 | Q 0.4 | DO | SPARE_7_4 | Spare | - | - | - | - | - | - | - | - | - | - |  |  | N | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 7 | 5 | Q 0.5 | DO | SPARE_7_5 | Spare | - | - | - | - | - | - | - | - | - | - |  |  | N | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 7 | 6 | Q 0.6 | DO | SPARE_7_6 | Spare | - | - | - | - | - | - | - | - | - | - |  |  | N | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 7 | 7 | Q 0.7 | DO | SPARE_7_7 | Spare | - | - | - | - | - | - | - | - | - | - |  |  | N | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 7 | 8 | Q 1.0 | DO | SPARE_7_8 | Spare | - | - | - | - | - | - | - | - | - | - |  |  | N | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 7 | 9 | Q 1.1 | DO | SPARE_7_9 | Spare | - | - | - | - | - | - | - | - | - | - |  |  | N | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 7 | 10 | Q 1.2 | DO | SPARE_7_10 | Spare | - | - | - | - | - | - | - | - | - | - |  |  | N | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 7 | 11 | Q 1.3 | DO | SPARE_7_11 | Spare | - | - | - | - | - | - | - | - | - | - |  |  | N | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 7 | 12 | Q 1.4 | DO | SPARE_7_12 | Spare | - | - | - | - | - | - | - | - | - | - |  |  | N | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 7 | 13 | Q 1.5 | DO | SPARE_7_13 | Spare | - | - | - | - | - | - | - | - | - | - |  |  | N | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 7 | 14 | Q 1.6 | DO | SPARE_7_14 | Spare | - | - | - | - | - | - | - | - | - | - |  |  | N | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 7 | 15 | Q 1.7 | DO | PLC05_WATCHDOG | PLC05 Watchdog Output Pulses 10secs ON , 9 OFF | OFF | ON | - | - | - | FDS | A1 | Chemical | - | - | DO |  | N | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | N | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | N | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | N | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[25 empty] | Norm DI Used | Norm DI Spare | Norm DO Used | Norm DO Spare | Norm AI Used | Norm AI Spare | Norm AO Used | Norm AO Spare | Dty DI Used | Dty DI Spare | Dty DO Used | Dty DO Spare | Dty AI Used | Dty AI Spare | Dty AO Used | Dty AO Spare | S/B DI Used | S/B DI Spare | S/B DO Used | S/B DO Spare | S/B AI Used | S/B AI Spare | S/B AO Used | S/B AO Spare | Ast DI Used | Ast DI Spare | Ast DO Used | Ast DO Spare | Ast AI Used | Ast AI Spare | Ast AO Used | Ast AO Spare
[25 empty] | 26 | 6 | 3 | 13 | 1 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[26 empty] | Norm DI % Spare |  | Norm DO % Spare |  | Norm AI % Spare |  | Norm AO % Spare |  | Dty DI % Spare |  | Dty DO % Spare |  | Dty AI % Spare |  | Dty AO % Spare |  | S/B DI % Spare |  | S/B DO % Spare |  | S/B AI % Spare |  | S/B AO % Spare |  | Ast DI % Spare |  | Ast DO % Spare |  | Ast AI % Spare |  | Ast AO % Spare
[26 empty] | 18.75 |  | 81.25 |  | 87.5 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
[25 empty] | Norm Total I/O | Norm Total Spare | Norm Total % Spare | [5 empty] | Dty Total I/O | Dty Total Spare | Dty Total % Spare | [5 empty] | S/B Total I/O | S/B Total Spare | S/B Total % Spare | [5 empty] | Ast Total I/O | Ast Total Spare | Ast Total % Spare
[25 empty] | 30 | 26 | 46.4286 | [5 empty] | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0
DI
DI-Duty
DI-Standby
DI-Assist
DO
DO-Duty
DO-Standby
DO-Assist
AI
AI-Duty
AI-Standby
AI-Assist
AO
AO-Duty
AO-Standby
AO-Assist
Note on T12: LT80: Fill this column as required: - N, D, S, A (CAPS)

## PLC#05 Soft IO Count
Project Title: United Utilities - Tyldesley UID PLC05 - Chemical Dosing
UUID: 80021608_02
Contract Title: System Integration
Document Title: Software Design Specification
SDS Annexure
Soft I / O Database
Duty D, Standby S, Assist A, Instrument I
[23 empty] | Byte = | 1
DP Node No | Number of bytes alloted |  | Addresses |  |  |  | Signal type | Inst / PLC Tag | Description | State 0 | State 1 | Range | Engg. Unit | Reference Document Number | Document Description | Doc. Rev. | Process Unit | Model Name | GSD |  |  |  | Word = | 2
| Inputs | Outputs | Inputs |  | Outputs | [17 empty] | Double = | 4
| DB132 | DB133 | HW Config (Rack ref) | DB130 | HW Config (Rack ref) | DB131 | [14 empty] | DI | D0 | AI | AO | DI Dty | DI S/B | DI Ast | DI Inst | DO Dty | DO S/B | DO Ast | DO Inst | AI Dty | AI S/B | AI Ast | AI Inst | AO Dty | AO S/B | AO Ast | AO Inst
DP Master: |  | 2 | Master Port: | CP315-2PN/DP (Rack 0, Slot 2) |  |  | DP Link:
11 | 68 | [6 empty] | CP02 | Incomer Power Meter |  |  |  |  | WIG0179/80021608/01/13/71005 | P&ID | 0 | Chemical | Diris | DIRI0948v3.GSD | D | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW0 |  |  | DP-AI | CP02_CR_PHS1 | Incomer Power Meter Phase 1 Current |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW2 |  |  | DP-AI | CP02_CR_PHS2 | Incomer Power Meter Phase 2 Current |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW4 |  |  | DP-AI | CP02_CR_PHS3 | Incomer Power Meter Phase 3 Current |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW6 |  |  | DP-AI | CP02_CR_NEU | Incomer Power Meter Neutral Current |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW8 |  |  | DP-AI | CP02_VT12_P2P | Incomer Power Meter Phase to phase Voltage U12 |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW10 |  |  | DP-AI | CP02_VT23_P2P | Incomer Power Meter Phase to phase Voltage U23 |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW12 |  |  | DP-AI | CP02_VT31_P2P | Incomer Power Meter Phase to phase Voltage U31 |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW14 |  |  | DP-AI | CP02_VT1_P2N | Incomer Power Meter Phase to neutral voltage phase 1 |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW16 |  |  | DP-AI | CP02_VT2_P2N | Incomer Power Meter Phase to neutral voltage phase 2 |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW18 |  |  | DP-AI | CP02_VT3_P2N | Incomer Power Meter Phase to neutral voltage phase 3 |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW20 |  |  | DP-AI | CP02_FRQ | Incomer Power Meter Frequency |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW22 |  |  | DP-AI | CP02_PR_ACT | Incomer Power Meter S Active Power +/- |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW24 |  |  | DP-AI | CP02_PR_RCTIV | Incomer Power Meter S Reactive Power +/- |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW26 |  |  | DP-AI | CP02_PR_APPR | Incomer Power Meter S Apparent Power +/- |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW28 |  |  | DP-AI | CP02_PR_FCT | Incomer Power Meter S Power factor L/C (-: Capacitive and +: Inductive [0.001]) |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW30 |  |  | DP-AI | CP02_I1MX | Incomer Power Meter I1 max |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW32 |  |  | DP-AI | CP02_I2MX | Incomer Power Meter I2 max |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW34 |  |  | DP-AI | CP02_I3MX | Incomer Power Meter I3 max |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW36 |  |  | DP-AI | CP02_PR_ACTMX_P | Incomer Power Meter Maximum value active power + |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW38 |  |  | DP-AI | CP02_PR_ACTMX_M | Incomer Power Meter Maximum value active power - |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW40 |  |  | DP-AI | CP02_PR_RACTMX_P | Incomer Power Meter Maximum value reactive power + |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW42 |  |  | DP-AI | CP02_PR_RACTMX_M | Incomer Power Meter Maximum value reactive power - |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW44 |  |  | DP-AI | CP02_PR_APPRMX | Incomer Power Meter Maximum apparent power |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW46 |  |  | DP-AI | CP02_NRG_ACT_L0 | Incomer Power Meter Active energy + < 10,000 |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW48 |  |  | DP-AI | CP02_NRG_ACT_HI | Incomer Power Meter Active energy + > 10,000 |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW50 |  |  | DP-AI | CP02_NRG_RACT_L0 | Incomer Power Meter Reactive energy + < 10,000 |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW52 |  |  | DP-AI | CP02_NRG_RACT_HI | Incomer Power Meter Reactive energy + > 10,000 |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW54 |  |  | DP-AI | CP02_NRG_APPR_L0 | Incomer Power Meter Apparent energy < 10,000 |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW56 |  |  | DP-AI | CP02_NRG_APPR_HI | Incomer Power Meter Apparent energy > 10,000 |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW58 |  |  | DP-AI | CP02_SYS_I | Incomer Power Meter System I |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW60 |  |  | DP-AI | CP02_SYS_U | Incomer Power Meter System U |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW62 |  |  | DP-AI | CP02_SYS_V | Incomer Power Meter System V |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW64 |  |  | DP-AI | CP02_HR_MTR_LO | Incomer Power Meter Hour meter < 10,000 |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW66 |  |  | DP-AI | CP02_HR_MTR_HI | Incomer Power Meter Hour meter > 10,000 |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 4 | [6 empty] | A5-LIT315 | Chemical Tank Level |  |  |  |  | WIG0179/80021608/01/13/71005 | P&ID | 0 | Chemical | Pulsar | PULSE07E2.GSD | D | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW68 |  |  | DP-DI | A5_LIT315_LEVEL | Chemical Tank Level Liquid Level in mm - Profibus 0.0 |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW70 |  |  | DP-DI | A5_LIT315_DISTANCE | Chemical Tank Level Distance from Transducer in mm - Profibus 2.0 |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW72 |  |  | DP-DI | A5_LIT315_CONFIDENCE | Chemical Tank Level Confidence in % - Profibus 4.0 |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW74 |  |  | DP-DI | A5_LIT315_STRENGTH | Chemical Tank Level Signal Strength in dB x 10 - Profibus 6.0 |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW76 |  |  | DP-DI | A5_LIT315_HALL | Chemical Tank Level Hall- Profibus 8.0 |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW78 |  |  | DP-DI | A5_LIT315_AVA_NOISE | Chemical Tank Level Average Noise - Profibus 10.0 |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW80 |  |  | DP-DI | A5_LIT315_PEAK_NOISE | Chemical Tank Level Peak Noise - Profibus 12.0 |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW82 |  |  | DP-DI | A5_LIT315_TEMP | Chemical Tank Level Temperature - Profibus 12.0 |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW84 |  |  | DP-DI | A5_LIT315_RELAY_STATUS | Chemical Tank Level Relay Status - Profibus 16.0 |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW86 |  |  | DP-DI | A5_LIT315_DIG_IN | Chemical Tank Level Digital Input Status - Profibus 18.0 |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW88 |  |  | DP-DI | A5_LIT315_USONIC | Chemical Tank Level Ultrasonic Status 3 is OK- Profibus 20.0 |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 4 | [6 empty] | A5-LIT323 | Blind Tank Level |  |  |  |  | WIG0179/80021608/01/13/71005 | P&ID | 0 | Chemical | Pulsar | PULSE07E2.GSD | D | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW90 |  |  | DP-DI | A5_LIT323_LEVEL | Blind Tank Level Liquid Level in mm - Profibus 0.0 |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW92 |  |  | DP-DI | A5_LIT323_DISTANCE | Blind Tank Level Distance from Transducer in mm - Profibus 2.0 |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW94 |  |  | DP-DI | A5_LIT323_CONFIDENCE | Blind Tank Level Confidence in % - Profibus 4.0 |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW96 |  |  | DP-DI | A5_LIT323_STRENGTH | Blind Tank Level Signal Strength in dB x 10 - Profibus 6.0 |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW98 |  |  | DP-DI | A5_LIT323_HALL | Blind Tank Level Hall- Profibus 8.0 |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW100 |  |  | DP-DI | A5_LIT323_AVA_NOISE | Blind Tank Level Average Noise - Profibus 10.0 |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW102 |  |  | DP-DI | A5_LIT323_PEAK_NOISE | Blind Tank Level Peak Noise - Profibus 12.0 |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW104 |  |  | DP-DI | A5_LIT323_TEMP | Blind Tank Level Temperature - Profibus 12.0 |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW106 |  |  | DP-DI | A5_LIT323_RELAY_STATUS | Blind Tank Level Relay Status - Profibus 16.0 |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW108 |  |  | DP-DI | A5_LIT323_DIG_IN | Blind Tank Level Digital Input Status - Profibus 18.0 |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW110 |  |  | DP-DI | A5_LIT323_USONIC | Blind Tank Level Ultrasonic Status 3 is OK- Profibus 20.0 |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 4 | [6 empty] | A5-P504 | Chemical Dosing Pump |  |  |  |  | WIG0179/80021608/01/13/71005 | P&ID | 0 | Chemical | Grundfos | GRUN0971.GSD | D | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBB112 |  |  | DP-DI | A5_P504_CMD_ACK | Chemical Dosing Pump Command Acknowledge |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBB113 |  |  | DP-DI | A5_P504_SPARE_1 | Chemical Dosing Pump Spare |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBD114 |  |  | DP-DI | A5_P504_MAX_DOSE_FLW_ACK | Chemical Dosing Pump MaximumAllowedDosingFlowSetpoint |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBD118 |  |  | DP-DI | A5_P504_BUS_DOSE_FLW_ACK | Chemical Dosing Pump DosingFlowSetpointFromProfibus |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBX122.0 |  |  | DP-DI | A5_P504_RG | Chemical Dosing Pump Running Feedback |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBX122.1 |  |  | DP-DI | A5_P504_SPARE_2 | Chemical Dosing Pump Spare |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBX122.2 |  |  | DP-DI | A5_P504_SPARE_3 | Chemical Dosing Pump Spare |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBX122.3 |  |  | DP-DI | A5_P504_MAN_MODE | Chemical Dosing Pump Manual Mode |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBX122.4 |  |  | DP-DI | A5_P504_MAN_MODE1 | Chemical Dosing Pump Manual Mode |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBX122.5 |  |  | DP-DI | A5_P504_MAN_MODE2 | Chemical Dosing Pump Manual Mode |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBX122.6 |  |  | DP-DI | A5_P504_ANTICAVIT_EN | Chemical Dosing Pump Anti-cavitation Status |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBX122.7 |  |  | DP-DI | A5_P504_AUTO_RESTRT_EN | Chemical Dosing Pump Auto Restart After Alarm Status |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBX123.0 |  |  | DP-DI | A5_P504_SPARE_4 | Chemical Dosing Pump Spare |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBX123.1 |  |  | DP-DI | A5_P504_SPARE_5 | Chemical Dosing Pump Spare |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBX123.2 |  |  | DP-DI | A5_P504_SPARE_6 | Chemical Dosing Pump Spare |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBX123.3 |  |  | DP-DI | A5_P504_SPARE_7 | Chemical Dosing Pump Spare |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBX123.4 |  |  | DP-DI | A5_P504_SPARE_8 | Chemical Dosing Pump Spare |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBX123.5 |  |  | DP-DI | A5_P504_BUT_STATUS | Chemical Dosing Pump Front Panel Button Status |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBX123.6 |  |  | DP-DI | A5_P504_WDG_STATUS | Chemical Dosing Pump Communication Status |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBX123.7 |  |  | DP-DI | A5_P504_SPARE_9 | Chemical Dosing Pump Spare |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBX124.0 |  |  | DP-DI | A5_P504_AV | Chemical Dosing Pump Available |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBX124.1 |  |  | DP-DI | A5_P504_AV1 | Chemical Dosing Pump Available |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBX124.2 |  |  | DP-DI | A5_P504_AV2 | Chemical Dosing Pump Available |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBX124.3 |  |  | DP-DI | A5_P504_ALM_STATUS | Chemical Dosing Pump Pending Status Alarm |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBX124.4 |  |  | DP-DI | A5_P504_SPARE_10 | Chemical Dosing Pump Spare |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBX124.5 |  |  | DP-DI | A5_P504_CALIB_EN | Chemical Dosing Pump Calibration Mode Status |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBX124.6 |  |  | DP-DI | A5_P504_BLEED_EN | Chemical Dosing Pump Bleeding Status |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBX124.7 |  |  | DP-DI | A5_P504_SPARE_11 | Chemical Dosing Pump Spare |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBB125 |  |  | DP-DI | A5_P504_ALM_CODE | Chemical Dosing Pump Alarm Code |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW126 |  |  | DP-DI | A5_P504_RUN_HRS | Chemical Dosing Pump Run Hours ( 2 hrs counter ) |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW128 |  |  | DP-DI | A5_P504_POWER_COUNTER | Chemical Dosing Pump No. of Power Ups |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBD130 |  |  | DP-DI | A5_P504_STROKE_COUNTER | Chemical Dosing Pump Stroke Counter |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBD134 |  |  | DP-DI | A5_P504_ACT_DOSE_FLOW | Chemical Dosing Pump Actual Dosing Flow |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBX138.0 |  |  | DP-DI | A5_P504_S_INT1 | Chemical Dosing Pump Safety Interlock1 Level Alarm |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBX138.1 |  |  | DP-DI | A5_P504_S_INT2 | Chemical Dosing Pump Safety Interlock1 Level Warning |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBX138.2 |  |  | DP-DI | A5_P504_E_STOP | Chemical Dosing Pump External Stop input |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBX138.3 |  |  | DP-DI | A5_P504_DP_INP_1 | Chemical Dosing Pump Drive Protect – Monitor Input |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBX138.4 |  |  | DP-DI | A5_P504_DP_INP_2 | Chemical Dosing Pump Drive Protect – Leakage/Diaphragm |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBX138.5 |  |  | DP-DI | A5_P504_IP_5 | Chemical Dosing Pump Pulse Input |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBX138.6 |  |  | DP-DI | A5_P504_SPARE_12 | Chemical Dosing Pump Spare |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBX138.7 |  |  | DP-DI | A5_P504_SPARE_13 | Chemical Dosing Pump Spare |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBX139.0 |  |  | DP-DI | A5_P504_SPARE_14 | Chemical Dosing Pump Spare |  |  | - | - | [6 empty] | D | 1 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW140 |  |  | DP-AI | A5_P504_ANALOG_INPUT | Chemical Dosing Pump Analogue Input |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBD142 |  |  | DP-AI | A5_P504_MAN_DOS_FLOW | Chemical Dosing Pump Dosing Flow in Manual |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW146 |  |  | DP-AI | A5_P504_MAX_PUMP_FLOW | Chemical Dosing Pump Maximum Pump Flow |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBB148 |  |  | DP-AI | A5_P504_WARNING_CODE | Chemical Dosing Pump Actual Warning Code |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBB149 |  |  | DP-AI | A5_P504_ALM_CODE_DISP | Chemical Dosing Pump Identical to Alarm Code |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBD150 |  |  | DP-AI | A5_P504_PULSE_DOSE_VOL | Chemical Dosing Pump Dosing Vol in Pulse Dosing Cntrl |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBD154 |  |  | DP-AI | A5_P504_BATCH_DOSE_VOL | Chemical Dosing Pump Dosing Vol in Batch Dosing Cntrl |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBD158 |  |  | DP-AI | A5_P504_TIMER_DOSE_VOL | Chemical Dosing Pump Dosing Vol in Timer Dosing Cntrl |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW162 |  |  | DP-AI | A5_P504_TIMER_DOSE_PRD | Chemical Dosing Pump Dosing Period in Timer Dosing Cntrl |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBW164 |  |  | DP-AI | A5_P504_TIMER_DOSE_SRT | Chemical Dosing Pump Dosing Start Time in TimerDosngCntrl |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBD166 |  |  | DP-AI | A5_P504_CALIB_VOL | Chemical Dosing Pump Calibration Value |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBB170 |  |  | DP-AI | A5_P504_LED_CONTROL | Chemical Dosing Pump Status of Green and Red LEDs |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBB171 |  |  | DP-AI | A5_P504_TEMP | Chemical Dosing Pump Temperature |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBB172 |  |  | DP-AI | A5_P504_MAX_PUMP_PRESS | Chemical Dosing Pump Maximum Pressure |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBB173 |  |  | DP-AI | A5_P504_LANGUAGE | Chemical Dosing Pump Language for Display |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBB174 |  |  | DP-AI | A5_P504_SOFT_VERSION | Chemical Dosing Pump Software Version |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBB175 |  |  | DP-AI | A5_P504_PROFIBUS_SW_VR | Chemical Dosing Pump Profibus Software Version |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBB176 |  |  | DP-AI | A5_P504_INPUT_SETUP1 | Chemical Dosing Pump Setup of Inputs |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBB177 |  |  | DP-AI | A5_P504_SCALE_SETUP1 | Chemical Dosing Pump Units to Appear in the Display |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBB178 |  |  | DP-AI | A5_P504_ANTICAV_SETUP | Chemical Dosing Pump Anti-Cavitation Setup |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DB132.DBB179 |  |  | DP-AI | A5_P504_INPUT_SETUP2 | Chemical Dosing Pump Setup of Inputs 2 |  |  | - | - | [6 empty] | D | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DP Node No | Number of bytes alloted |  | Addresses |  |  |  | Signal type | Inst / PLC Tag | Description | State 0 | State 1 | Range | Engg. Unit | Reference Document Number | Document Description | Doc. Rev. | Process Unit | Model Name | GSD
| Inputs | Outputs | Inputs |  | Outputs
| DB132 | DB133 | HW Config (Rack ref) | DB130 | HW Config (Rack ref) | DB131
11 |  | 32 | [5 empty] | CP02 | Incomer Power Meter |  |  | - | - | WIG0179/80021608/01/13/71005 | P&ID | 0 | Chemical | Telemec. Altivar ATV61 | TELE09CD.GSD | D | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | DB133.DBD0 | DP-AO | CP02_SPARE00 | Incomer Power Meter | - | - | - | - | [6 empty] | D | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
[6 empty] | DB133.DBD4 | DP-AO | CP02_SPARE01 | Incomer Power Meter | - | - | - | - | [6 empty] | D | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
[6 empty] | DB133.DBD8 | DP-AO | CP02_SPARE02 | Incomer Power Meter | - | - | - | - | [6 empty] | D | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
[6 empty] | DB133.DBD12 | DP-AO | CP02_SPARE03 | Incomer Power Meter | - | - | - | - | [6 empty] | D | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
[6 empty] | DB133.DBD16 | DP-AO | CP02_SPARE04 | Incomer Power Meter | - | - | - | - | [6 empty] | D | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
[6 empty] | DB133.DBD20 | DP-AO | CP02_SPARE05 | Incomer Power Meter | - | - | - | - | [6 empty] | D | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
[6 empty] | DB133.DBD24 | DP-AO | CP02_SPARE06 | Incomer Power Meter | - | - | - | - | [6 empty] | D | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
[6 empty] | DB133.DBW28 | DP-AO | CP02_SPARE07 | Incomer Power Meter | - | - | - | - | [6 empty] | D | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
14 |  | 22 | [5 empty] | A5-P504 | Chemical Dosing Pump |  |  | - | - | WIG0179/80021608/01/13/71005 | P&ID | 0 | Chemical | Grundfos | GRUN0971.GSD | D | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | DB133.DBB30 | DP-DO | A5_P504_CMD_BUFFER_1 | Chemical Dosing Pump Cmds from PLC to Pump | - | - | - | - | [6 empty] | D | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | DB133.DBB31 | DP-DO | A5_P504_CMD_BUFFER_2 | Chemical Dosing Pump Cmds from PLC to Pump | - | - | - | - | [6 empty] | D | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | DB133.DBB32 | DP-AO | A5_P504_CMD_BUFFER_3 | Chemical Dosing Pump Cmds from PLC to Pump | - | - | - | - | [6 empty] | D | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
[6 empty] | DB133.DBB33 | DP-AO | A5_P504_CMD_BUFFER_4 | Chemical Dosing Pump Cmds from PLC to Pump | - | - | - | - | [6 empty] | D | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
[6 empty] | DB133.DBD34 | DP-AO | A5_P504_CMD_BUFFER_DI | Chemical Dosing Pump Data Items from PLC to Pump | - | - | - | - | [6 empty] | D | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
[8 empty] | Process Unit | Description
[25 empty] | DI Dty | DI S/B | DI Ast | DI Inst | DO Dty | DO S/B | DO Ast | DO Inst | AI Dty | AI S/B | AI Ast | AI Inst | AO Dty | AO S/B | AO Ast | AO Inst
[25 empty] | 8 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 11 | 0 | 0 | 0

## Network Load
Project Title: United Utilities - Tyldesley UID PLC05 - Chemical Dosing
UUID: 80021608_02
Contract Title: System Integration
Document Title: Software Design Specification
SDS Annexure
Network Calculation
Ethernet Load
No. | Tag type | Number of Bits | Number of Bytes | Number of Words | Number of Dwords | Spare | Network Load in Byte
1 | Tag Database | 73 | 2 | 26 | 48 | 0 | 264
2 | Alarm Schedule | 57 | 0 | 0 | 0 | 0
3 | PLC to Telemetry | 16 | 0 | 0 | 3 | 0
| Total | 146 | 2 | 26 | 48 | 0
Profibus Load
No. | Tag type | Number of Bits | Number of Bytes | Number of Words | Number of Dwords | Spare | Network Load in Byte
1 | Inputs | 0 | 20 | 0 | 0 | 0 | 28
2 | Outputs | 0 | 8 | 0 | 0 | 0
| Total | 0 | 28 | 0 | 0 | 0

## PLC#05 Tag Database
Project Title: United Utilities - Tyldesley UID PLC05 - Chemical Dosing
UUID: 80021608_02
Contract Title: System Integration
Document Title: Software Design Specification
| Cougar Project No. |  |  |  | Client Ref:
SDS Annexure
Standard SCADA & HMI TAGS
PLC Tag | PLC Tag Description | Data | Tag | Status | Status | Range |  | Set Point |  |  |  | Decimal | Scaling | Trend Logging |  |  | Report | Status | Selection | HMI | SCADA | Process | SI | PP | Remarks
|  | Type | Address | Off state | On state | Min | Max | Default | Min | Max | Units | Places | Factor | HMI | SCADA | Samples | Logging | Indication | & Control |  |  | Area | Checked | Checked
WTH | Words to HMI
CP02_RESET_TAD | Incomer Power Meter Date and Time | DATE_AND_TIME | DB360.DBD0 |  |  | - | - | - | - | - | - | - |  | - |  | - | - | - | - | Y
CP02_TOTAL | Incomer Power Meter Total | DINT | DB360.DBD8 |  |  | - | - | - | - | - | - | - |  | - |  | - | - | - | - | Y
A5_LIT315_DISPLAY | Chemical Tank Level Signal Status | INT | DB360.DBW12 |  |  | - | - | - | - | - | - | - |  | - |  | - | - | - | - | Y
A5_LIT315_PV | Chemical Tank Level Process Vari. (Eng Units) | REAL | DB360.DBD14 |  |  | - | - | - | - | - | - | - |  | - |  | - | - | - | - | Y
A5_LIT315_MIN_ENG | Chemical Tank Level Min Scale Value (Eng Units) | REAL | DB360.DBD18 |  |  | - | - | - | - | - | - | - |  | - |  | - | - | - | - | Y
A5_LIT315_MAX_ENG | Chemical Tank Level Max Scale Value (Eng Units) | REAL | DB360.DBD22 |  |  | - | - | - | - | - | - | - |  | - |  | - | - | - | - | Y
A5_LIT323_DISPLAY | Blind Tank Level Signal Status | INT | DB360.DBW26 |  |  | - | - | - | - | - | - | - |  | - |  | - | - | - | - | Y
A5_LIT323_PV | Blind Tank Level Process Vari. (Eng Units) | REAL | DB360.DBD28 |  |  | - | - | - | - | - | - | - |  | - |  | - | - | - | - | Y
A5_LIT323_MIN_ENG | Blind Tank Level Min Scale Value (Eng Units) | REAL | DB360.DBD32 |  |  | - | - | - | - | - | - | - |  | - |  | - | - | - | - | Y
A5_LIT323_MAX_ENG | Blind Tank Level Max Scale Value (Eng Units) | REAL | DB360.DBD36 |  |  | - | - | - | - | - | - | - |  | - |  | - | - | - | - | Y
A5_AV508_VALVE_MODE | Chemical Tank Outlet Valve Operating Mode | INT | DB360.DBW40 |  |  | 0 | 32678 | - | - | - | - | - |  | - |  | - | - | - | - | Y
A5_AV508_VALVE_STAT | Chemical Tank Outlet Valve Operating Status | INT | DB360.DBW42 |  |  | 0 | 32678 | - | - | - | - | - |  | - |  | - | - | - | - | Y
A5_AV508_PB_STAT | Chemical Tank Outlet Valve HMI Control Push Button Status | INT | DB360.DBW44 |  |  | 0 | 32678 | - | - | - | - | - |  | - |  | - | - | - | - | Y
A5_FIT112_DISPLAY | Chemical Dosing Pump Delivery Flowmeter Signal Status | INT | DB360.DBW46 |  |  | - | - | - | - | - | - | - |  | - |  | - | - | - | - | Y
A5_FIT112_PV | Chemical Dosing Pump Delivery Flowmeter Process Vari. (Eng Units) | REAL | DB360.DBD48 |  |  | 0 | 625 | - | - | - | l/hr | - |  | - |  | - | - | - | - | Y
A5_FIT112_MIN_ENG | Chemical Dosing Pump Delivery Flowmeter Min Scale Value (Eng Units) | REAL | DB360.DBD52 |  |  | 0 | 625 | - | - | - | l/hr | - |  | - |  | - | - | - | - | Y
A5_FIT112_MAX_ENG | Chemical Dosing Pump Delivery Flowmeter Max Scale Value (Eng Units) | REAL | DB360.DBD56 |  |  | 0 | 625 | - | - | - | l/hr | - |  | - |  | - | - | - | - | Y
A5_P504_DRV_MODE | Chemical Dosing Pump - Operating Mode | INT | DB360.DBW60 |  |  |  |  | - | - | - | - | - |  | - |  | - | - | - | - | Y
A5_P504_DRV_STAT | Chemical Dosing Pump - Operating Status | INT | DB360.DBW62 |  |  |  |  | - | - | - | - | - |  | - |  | - | - | - | - | Y
A5_P504_FLC | Chemical Dosing Pump - Full Load Current | INT | DB360.DBW64 |  |  | 0 | FLC | - | - | - | - | - |  | - |  | - | - | - | - | Y
A5_P504_HRS_RUN | Chemical Dosing Pump - Cumulative Hours Run | INT | DB360.DBW66 |  |  |  |  | - | - | - | - | - |  | - |  | - | - | - | - | Y
A5_P504_I_AMP | Chemical Dosing Pump - Current in Amp | INT | DB360.DBW68 |  |  |  |  | - | - | - | - | - |  | - |  | - | - | - | - | Y
A5_P504_MODE | Chemical Dosing Pump - Control Mode | INT | DB360.DBW70 |  |  |  |  | - | - | - | - | - |  | - |  | - | - | - | - | Y
A5_P504_PB_STAT | Chemical Dosing Pump - HMI Control PB Status | INT | DB360.DBW72 |  |  |  |  | - | - | - | - | - |  | - |  | - | - | - | - | Y
A5_P504_SPD_ACT | Chemical Dosing Pump - Actual Speed | INT | DB360.DBW74 |  |  | 0 | 32678 | - | - | - | - | - |  | - |  | - | - | - | - | Y
A5_P504_ACTL_FLOW | Chemical Dosing Pump - Actual Flow | REAL | DB360.DBD76 |  |  |  |  | - | - | - | - | - |  | - |  | - | - | - | - | Y
A5_P504_CNTRL_MODE | Chemical Dosing Pump - Pump Control Mode | INT | DB360.DBW80 |  |  |  |  | - | - | - | - | - |  | - |  | - | - | - | - | Y
A5_P504_CONFG_PB_STAT | Chemical Dosing Pump - Configuration Pushbutton Status | BYTE | DB360.DBB82 |  |  |  |  | - | - | - | - | - |  | - |  | - | - | - | - | Y
A5_P504_DOSE_SPEED | Chemical Dosing Pump - Ref Speed for HMI display | REAL | DB360.DBD84 |  |  |  |  | - | - | - | - | - |  | - |  | - | - | - | - | Y
A5_P504_DUTY_STAT | Chemical Dosing Pump - Duty Cycle | INT | DB360.DBW88 |  |  |  |  | - | - | - | - | - |  | - |  | - | - | - | - | Y
A5_P504_DOSE_LTR_HRS | Chemical Dosing Pump - Pump Dose flow l/h | REAL | DB360.DBD90 |  |  |  |  | - | - | - | - | - |  | - |  | - | - | - | - | Y
A5_P504_MAX_DOSE_FLOW | Chemical Dosing Pump - Maximum Dose Flow | REAL | DB360.DBD94 |  |  |  |  | - | - | - | - | - |  | - |  | - | - | - | - | Y
A5_P504_POWER_COUNTER | Chemical Dosing Pump - Qty of Powered Up's | INT | DB360.DBW98 |  |  |  |  | - | - | - | - | - |  | - |  | - | - | - | - | Y
A5_P504_SPD_PER | Chemical Dosing Pump - Pump Speed in Percentage | REAL | DB360.DBD100 |  |  |  |  | - | - | - | - | - |  | - |  | - | - | - | - | Y
A5_P504_STATUS | Chemical Dosing Pump - Status (Duty/Standby/Assist) | INT | DB360.DBW104 |  |  |  |  | - | - | - | - | - |  | - |  | - | - | - | - | Y
A5_P504_STROKE_COUNT | Chemical Dosing Pump - Stroke Counter | DINT | DB360.DBD106 |  |  |  |  | - | - | - | - | - |  | - |  | - | - | - | - | Y
A5_INLETFLOW312 | Derived Inlet Flow into Detention Tank | REAL | DB360.DBD110 |  |  |  |  | - | - | - | - | - |  | - |  | - | - | - | - | Y
ACTUAL_FLOW_RATIO | Actual Ratio of Dosage Flow and Detention Tank Inlet Flow | REAL | DB360.DBD114 |  |  |  |  | - | - | - | - | - |  | - |  | - | - | - | - | Y
A5_MAX_DOSE_FLOW | Maximum Dose Flow | REAL | DB360.DBD118 |  |  |  |  | - | - | - | - | - |  | - |  | - | - | - | - | Y
ChngeInDetentioTnkLvl | Change in Detention Tank level | REAL | DB360.DBD122 |  |  |  |  | - | - | - | - | - |  | - |  | - | - | - | - | Y
A5_P504_SP | Dosing Setpoint to be sent to the Grundfos Drive | REAL | DB360.DBD126 |  |  |  |  | - | - | - | - | - |  | - |  | - | - | - | - | Y
BTH | Bits to HMI
A5_LIT315_HH_STATE | Chemical Tank Level Hi-Hi State | BOOL | DB361.DBX0.0 | - | - | [14 empty] | Y
A5_LIT315_H_STATE | Chemical Tank Level High State | BOOL | DB361.DBX0.1 | - | - | [14 empty] | Y
A5_LIT315_L_STATE | Chemical Tank Level Low State | BOOL | DB361.DBX0.2 | - | - | [14 empty] | Y
A5_LIT315_LL_STATE | Chemical Tank Level Lo-Lo State | BOOL | DB361.DBX0.3 | - | - | [14 empty] | Y
A5_LIT315_OOR | Chemical Tank Level Signal OOR State | BOOL | DB361.DBX0.4 | - | - | [14 empty] | Y
A5_LIT315_HLTHY | Chemical Tank Level Inst. Healthy State | BOOL | DB361.DBX0.5 | - | - | [14 empty] | Y
A5_LIT323_HH_STATE | Blind Tank Level Hi-Hi State | BOOL | DB361.DBX0.6 | - | - | [14 empty] | Y
A5_LIT323_H_STATE | Blind Tank Level High State | BOOL | DB361.DBX0.7 | - | - | [14 empty] | Y
A5_LIT323_L_STATE | Blind Tank Level Low State | BOOL | DB361.DBX1.0 | - | - | [14 empty] | Y
A5_LIT323_LL_STATE | Blind Tank Level Lo-Lo State | BOOL | DB361.DBX1.1 | - | - | [14 empty] | Y
A5_LIT323_OOR | Blind Tank Level Signal OOR State | BOOL | DB361.DBX1.2 | - | - | [14 empty] | Y
A5_LIT323_HLTHY | Blind Tank Level Inst. Healthy State | BOOL | DB361.DBX1.3 | - | - | [14 empty] | Y
A5_LS316_STATE | Chemical Tank High High Level State | BOOL | DB361.DBX1.4 | - | - | [14 empty] | Y
A5_AV508_A_AV | Chemical Tank Outlet Valve Healthy Output | BOOL | DB361.DBX1.5 | - | Healthy | [14 empty] | Y
A5_AV508_A_FTO | Chemical Tank Outlet Valve Failed To Open Fault | BOOL | DB361.DBX1.6 | - | Failed | [14 empty] | Y
A5_AV508_A_FTC | Chemical Tank Outlet Valve Failed To Close Fault | BOOL | DB361.DBX1.7 | - | Failed | [14 empty] | Y
A5_AV508_A_LS_FLT | Chemical Tank Outlet Valve Limit Switch Fault | BOOL | DB361.DBX2.0 | - | Failed | [14 empty] | Y
A5_AV508_S_INT | Chemical Tank Outlet Valve Safety Interlock Healthy | BOOL | DB361.DBX2.1 | - | Healthy | [14 empty] | Y
A5_LS318_STATE | Chemical Dosing Pump PRV Catch Pot State | BOOL | DB361.DBX2.2 | - | - | [14 empty] | Y
A5_FIT112_HH_STATE | Chemical Dosing Pump Delivery Flowmeter Hi-Hi State | BOOL | DB361.DBX2.3 | - | - | [14 empty] | Y
A5_FIT112_H_STATE | Chemical Dosing Pump Delivery Flowmeter High State | BOOL | DB361.DBX2.4 | - | - | [14 empty] | Y
A5_FIT112_L_STATE | Chemical Dosing Pump Delivery Flowmeter Low State | BOOL | DB361.DBX2.5 | - | - | [14 empty] | Y
A5_FIT112_LL_STATE | Chemical Dosing Pump Delivery Flowmeter Lo-Lo State | BOOL | DB361.DBX2.6 | - | - | [14 empty] | Y
A5_FIT112_OOR | Chemical Dosing Pump Delivery Flowmeter Signal OOR State | BOOL | DB361.DBX2.7 | - | - | [14 empty] | Y
A5_FIT112_HLTHY | Chemical Dosing Pump Delivery Flowmeter Inst. Healthy State | BOOL | DB361.DBX3.0 | - | - | [14 empty] | Y
A5_LS319_STATE | Chemical Dosing Skid Drip Tray High Level State | BOOL | DB361.DBX3.1 | - | - | [14 empty] | Y
A5_LS320_STATE | Chemical Dual Containment Catch Pot State | BOOL | DB361.DBX3.2 | - | - | [14 empty] | Y
A5_LS321_STATE | Chemical Dosing Dual Containment Enclosure Level State | BOOL | DB361.DBX3.3 | - | - | [14 empty] | Y
A5_LS317_STATE | Chemical Tank High Level State | BOOL | DB361.DBX3.4 | - | - | [14 empty] | Y
A5_XS201_STATE | Emergency Eyewash 1 State | BOOL | DB361.DBX3.5 | - | - | [14 empty] | Y
A5_XS202_STATE | Emergency Eyewash 2 State | BOOL | DB361.DBX3.6 | - | - | [14 empty] | Y
A5_XS203_STATE | Emergency Shower State | BOOL | DB361.DBX3.7 | - | - | [14 empty] | Y
A5_LS322_STATE | Emergency Shower Low Level Switch State | BOOL | DB361.DBX4.0 | - | - | [14 empty] | Y
A5_LS324_STATE | Chemical Blind Tank High High State | BOOL | DB361.DBX4.1 | - | - | [14 empty] | Y
A5_TS601_STATE | Emergency Shower Low Temperature Switch State | BOOL | DB361.DBX4.2 | - | - | [14 empty] | Y
A5_P504_A_AV | Chemical Dosing Pump - Healthy Output | BOOL | DB361.DBX4.3 | [16 empty] | Y
A5_P504_A_FTR | Chemical Dosing Pump - Fail to Run Fault | BOOL | DB361.DBX4.4 | [16 empty] | Y
A5_P504_A_FTRSP | Chemical Dosing Pump - Fail to Reach Setpoint Fault | BOOL | DB361.DBX4.5 | [16 empty] | Y
A5_P504_A_FTS | Chemical Dosing Pump - Fail to Stop Fault | BOOL | DB361.DBX4.6 | [16 empty] | Y
A5_P504_ASSIST | Chemical Dosing Pump - Selected As Assist | BOOL | DB361.DBX4.7 | [16 empty] | Y
A5_P504_DUTY | Chemical Dosing Pump - Selected As Duty | BOOL | DB361.DBX5.0 | [16 empty] | Y
A5_P504_SBY | Chemical Dosing Pump - Selected As Standby | BOOL | DB361.DBX5.1 | [16 empty] | Y
A5_P504_ALM_RESTRT_EN | Chemical Dosing Pump - Auto Restart After Alarm | BOOL | DB361.DBX5.2 | [16 empty] | Y
A5_P504_ANALOG_REF_OOR | Chemical Dosing Pump - Analog Reference Out of Range | BOOL | DB361.DBX5.3 | [16 empty] | Y
A5_P504_ANTI_CAVIT_EN | Chemical Dosing Pump - Anti Cavitation Command | BOOL | DB361.DBX5.4 | [16 empty] | Y
A5_P504_BLEED_EN | Chemical Dosing Pump - Bleed Enable/Disable Command | BOOL | DB361.DBX5.5 | [16 empty] | Y
A5_P504_NODE_FLT | Chemical Dosing Pump - Dosing Pump 1 Profibus Node Fau | BOOL | DB361.DBX5.6 | [16 empty] | Y
A5_P504_SPARE | Chemical Dosing Pump - Spare | BOOL | DB361.DBX5.7 | [16 empty] | Y
A5_P504_WDG_EN | Chemical Dosing Pump - Communication Watchdog Command | BOOL | DB361.DBX6.0 | [16 empty] | Y
A5_P504_DME_EX_STOP | Chemical Dosing Pump | BOOL | DB361.DBX6.1 | [16 empty] | Y
MCC05_110V_FLD_STATE | MCC05110VSupplyHealthyState | BOOL | DB361.DBX6.2 |  | Healthy | [14 empty] | Y
MCC05_24V_A_STATE | MCC0524VAChemical-SupplyAHealthyState | BOOL | DB361.DBX6.3 |  | Healthy | [14 empty] | Y
MCC05_24V_B_STATE | MCC0524VBChemical-SupplyBHealthyState | BOOL | DB361.DBX6.4 |  | Healthy | [14 empty] | Y
MCC05_MAINS_FLD_STATE | ChemicalMCC05MainsSupplyHealthyState | BOOL | DB361.DBX6.5 |  | Healthy | [14 empty] | Y
PLC05_BUP_ON_STATE | PLC05BackupControlEnabledState | BOOL | DB361.DBX6.6 | PLC_Cntrl | Enabled | [14 empty] | Y
Chemical_Area_Alarms | Area Alarm | BOOL | DB361.DBX6.7 | [16 empty] | Y
WFH | Words from HMI
A5_LIT315_HH_SET | Chemical Tank Level Hi-Hi SP | REAL | DB362.DBD0 |  |  | - | - | - | - | - | % | - |  | - |  | - | - | NA | - | Y
A5_LIT315_H_SET | Chemical Tank Level High SP | REAL | DB362.DBD4 |  |  | - | - | - | - | - | % | - |  | - |  | - | - | NA | - | Y
A5_LIT315_L_SET | Chemical Tank Level Low SP | REAL | DB362.DBD8 |  |  | - | - | - | - | - | % | - |  | - |  | - | - | NA | - | Y
A5_LIT315_LL_SET | Chemical Tank Level Lo-Lo SP | REAL | DB362.DBD12 |  |  | - | - | - | - | - | % | - |  | - |  | - | - | NA | - | Y
A5_LIT323_HH_SET | Blind Tank Level Hi-Hi SP | REAL | DB362.DBD16 |  |  | - | - | - | - | - | % | - |  | - |  | - | - | NA | - | Y
A5_LIT323_H_SET | Blind Tank Level High SP | REAL | DB362.DBD20 |  |  | - | - | - | - | - | % | - |  | - |  | - | - | NA | - | Y
A5_LIT323_L_SET | Blind Tank Level Low SP | REAL | DB362.DBD24 |  |  | - | - | - | - | - | % | - |  | - |  | - | - | NA | - | Y
A5_LIT323_LL_SET | Blind Tank Level Lo-Lo SP | REAL | DB362.DBD28 |  |  | - | - | - | - | - | % | - |  | - |  | - | - | NA | - | Y
A5_FIT112_HH_SET | Chemical Dosing Pump Delivery Flowmeter Hi-Hi SP | REAL | DB362.DBD32 |  |  | 0 | 625 | - | - | - | l/hr | - |  | - |  | - | - | NA | - | Y
A5_FIT112_H_SET | Chemical Dosing Pump Delivery Flowmeter High SP | REAL | DB362.DBD36 |  |  | 0 | 625 | - | - | - | l/hr | - |  | - |  | - | - | NA | - | Y
A5_FIT112_L_SET | Chemical Dosing Pump Delivery Flowmeter Low SP | REAL | DB362.DBD40 |  |  | 0 | 625 | - | - | - | l/hr | - |  | - |  | - | - | NA | - | Y
A5_FIT112_LL_SET | Chemical Dosing Pump Delivery Flowmeter Lo-Lo SP | REAL | DB362.DBD44 |  |  | 0 | 625 | - | - | - | l/hr | - |  | - |  | - | - | NA | - | Y
A5_P504_FLT_TIME | Chemical Dosing Pump - Flow Fault Time | INT | DB362.DBW48 |  |  |  |  | - | - | - | % | - |  | - |  | - | - | NA | - | Y
A5_P504_MAN_SP | Chemical Dosing Pump - Manual Speed Setpoint | INT | DB362.DBW50 |  |  |  |  | - | - | - | % | - |  | - |  | - | - | NA | - | Y
A5_P504_MAX_DELIVERY | Chemical Dosing Pump - Max Delivery (Pm) | REAL | DB362.DBD52 |  |  |  |  | - | - | - | % | - |  | - |  | - | - | NA | - | Y
A5_P504_SPEED_SF | Chemical Dosing Pump - Speed Ref Scaling Factor | REAL | DB362.DBD56 |  |  |  |  | - | - | - | % | - |  | - |  | - | - | NA | - | Y
A5_P504_ANTI_CAVIT_ST | Chemical Dosing Pump - Anti-Cavitation Setup | BYTE | DB362.DBB60 |  |  |  |  | - | - | - | % | - |  | - |  | - | - | NA | - | Y
A5_P504_MAN_FLOW | Chemical Dosing Pump - Manual Flow | REAL | DB362.DBD62 |  |  |  |  | - | - | - | % | - |  | - |  | - | - | NA | - | Y
A5_P504_MAX_DOSE_FLOW | Chemical Dosing Pump - Maximum Dosing Flow | REAL | DB362.DBD66 |  |  |  |  | - | - | - | % | - |  | - |  | - | - | NA | - | Y
A5_P504_MAX_OUTPUT | Chemical Dosing Pump - Max output | REAL | DB362.DBD70 |  |  |  |  | - | - | - | % | - |  | - |  | - | - | NA | - | Y
A5_P504_MAX_SPEED | Chemical Dosing Pump - Max speed | REAL | DB362.DBD74 |  |  |  |  | - | - | - | % | - |  | - |  | - | - | NA | - | Y
A5_P504_MIN_SPEED | Chemical Dosing Pump - Min speed | REAL | DB362.DBD78 |  |  |  |  | - | - | - | % | - |  | - |  | - | - | NA | - | Y
A5_P504_SCAL_FACTOR | Chemical Dosing Pump - Scaling factor | REAL | DB362.DBD82 |  |  |  |  | - | - | - | % | - |  | - |  | - | - | NA | - | Y
A5_P504_SPARE | Chemical Dosing Pump - Spare | INT | DB362.DBW86 |  |  |  |  | - | - | - | % | - |  | - |  | - | - | NA | - | Y
A5_MAX_DOSE_FLOW_SP | Maximum Dose Flow_SP | REAL | DB362.DBD88 |  |  |  |  | - | - | - | % | - |  | - |  | - | - | NA | - | Y
CHEMICAL_REORDER_LVL | A5-LIT315 Chemical ReOrder Level | REAL | DB362.DBD92 |  |  |  |  | - | - | - | % | - |  | - |  | - | - | NA | - | Y
DOSING_RATE_PARTSMILLION | Dosing Rate – Parts Per Million | REAL | DB362.DBD96 |  |  |  |  | - | - | - | % | - |  | - |  | - | - | NA | - | Y
START_UP_FLOW | Start Up Flow | REAL | DB362.DBD100 |  |  |  |  | - | - | - | % | - |  | - |  | - | - | NA | - | Y
PROPORTIONALDOSINGTMR | Proportional Dosing Delay Timer | INT | DB362.DBW104 |  |  |  |  | - | - | - | % | - |  | - |  | - | - | NA | - | Y
STOPTMR_LVLSTPPDRISING | A5-LIT312 Dosing Stop Timer ( because Lvl hasnt risen ) | INT | DB362.DBW106 |  |  |  |  | - | - | - | % | - |  | - |  | - | - | NA | - | Y
DTNTNTNK_VOL_PER_VMTR | Detention Tnk Vol per Vertical mtr | REAL | DB362.DBD108 |  |  |  |  | - | - | - | % | - |  | - |  | - | - | NA | - | Y
ACTUALTANKHEIGHT | Actual Tank Height | REAL | DB362.DBD112 |  |  |  |  | - | - | - | % | - |  | - |  | - | - | NA | - | Y
LVLCHECKINTERVALTIMER | A5-LIT312 Level Check Interval Timer | INT | DB362.DBW116 |  |  |  |  | - | - | - | % | - |  | - |  | - | - | NA | - | Y
FLOWRATENOTREACHED | Flow Rate not reached | INT | DB362.DBW118 |  |  |  |  | - | - | - | % | - |  | - |  | - | - | NA | - | Y
FLOWSP_IF_FMETERFAILD | Preset flow SP for Pump if Flowmater has failed | REAL | DB362.DBD120 |  |  |  |  | - | - | - | % | - |  | - |  | - | - | NA | - | Y
IF_LIT312_FAILS_CNTNUE4 | If LIT312 fails – Dosing shall continue for | INT | DB362.DBW124 |  |  |  |  | - | - | - | - | - |  | - |  | - | - | NA | - | Y
BFH | Bits from HMI
Global_Reset | Global Latched Alarm Reset | BOOL | DB363.DBX0.0 | - | - | [14 empty] | Y
CP02_RESET | Incomer Power Meter Reset | BOOL | DB363.DBX0.1 | - | -
A5_AV508_PLC_MA | Chemical Tank Outlet Valve PLC Auto/Manual Mode Select (1= Manual, 0= Auto) | BOOL | DB363.DBX0.2 | Auto | Manual
A5_AV508_FLT_RST | Chemical Tank Outlet Valve Fault Reset Command | BOOL | DB363.DBX0.3 | - | Reset
A5_AV508_OPEN | Chemical Tank Outlet Valve Open Command (1= Open, 0= N/a) | BOOL | DB363.DBX0.4 | - | Open
A5_AV508_CLOSE | Chemical Tank Outlet Valve Close Command (1= Close, 0= N/a) | BOOL | DB363.DBX0.5 | - | Close
A5_P504_MAN_RUN | Chemical Dosing Pump - Start/Stop Command | BOOL | DB363.DBX0.6 | Stop | Start
A5_P504_PLC_MA | Chemical Dosing Pump - PLC Auto/Manual Mode Select | BOOL | DB363.DBX0.7 | Auto | Manual
A5_P504_SP_ANLG | Chemical Dosing Pump - Speed reference selected Analogue | BOOL | DB363.DBX1.0
A5_P504_SP_PROF | Chemical Dosing Pump - Speed reference selected Profibus | BOOL | DB363.DBX1.1
A5_P504_ALM_RESTRT_EN | Chemical Dosing Pump - Auto Restart After Alarm | BOOL | DB363.DBX1.2
A5_P504_ANTI_CAVIT_EN | Chemical Dosing Pump - Anti Cavitation Command | BOOL | DB363.DBX1.3
A5_P504_BLEED_EN | Chemical Dosing Pump - Bleed Enable/Disable Command | BOOL | DB363.DBX1.4
A5_P504_FLT_RST | Chemical Dosing Pump - Fault Reset | BOOL | DB363.DBX1.5
A5_P504_MCC_MA | Chemical Dosing Pump - MCC Mode Selection | BOOL | DB363.DBX1.6
A5_P504_PROFI_ANALOG | Chemical Dosing Pump - Profibus/Analog Selection | BOOL | DB363.DBX1.7
A5_P504_WDG_EN | Chemical Dosing Pump - Communication Watchdog Command | BOOL | DB363.DBX2.0
Data Summary
|  |  | Protocol | Bit Data Count | Byte Data Count | Word Data Count | Double Word Data Count | Total Data quantity Bytes) being transferred
|  |  |  | 12 | 3 | 31 | 30

## PLC#05 Alarm Schedule
Project Title: United Utilities - Tyldesley UID PLC05 - Chemical Dosing
UUID: 80021608_02
Contract Title: System Integration
Document Title: Software Design Specification | [9 empty] | 2014-02-12
SDS Annexure
Alarm Schedule
PLC Alarm Tag | Alarm Description | Data | Tag Address |  | Trigger | Alarm Parameter |  |  |  | HMI | SCADA | Process | SI | PP
|  | Type | Bit | Word | Bit | Priority | State | Ack | Reset |  |  | Area | Checked | Checked
A5_LIT315_HIHI_ALM | Chemical Tank Level - Hi-Hi | BOOL | DB309.DBX0.0 |  |  | High | Logic 1 | Y | Auto | Y |  | -
A5_LIT315_HI_ALM | Chemical Tank Level - High | BOOL | DB309.DBX0.1 |  |  | Medium | Logic 1 | Y | Auto | Y |  | -
A5_LIT315_LO_ALM | Chemical Tank Level - Low | BOOL | DB309.DBX0.2 |  |  | Medium | Logic 1 | Y | Auto | Y |  | -
A5_LIT315_LOLO_ALM | Chemical Tank Level - Lo-Lo | BOOL | DB309.DBX0.3 |  |  | High | Logic 1 | Y | Auto | Y |  | -
A5_LIT315_OTR_ALM | Chemical Tank Level - Out Of Range | BOOL | DB309.DBX0.4 |  |  | High | Logic 1 | Y | Supervisory | Y |  | -
A5_LIT315_INST_FLT_ALM | Chemical Tank Level - Inst Fault | BOOL | DB309.DBX0.5 |  |  | High | Logic 1 | Y | Supervisory | Y |  | -
A5_LIT315_NODE_FLT_ALM | Chemical Tank Level - Node Fault | BOOL | DB309.DBX0.6 |  |  | High | Logic 1 | Y | Supervisory | Y |  | -
A5_LIT323_HIHI_ALM | Blind Tank Level - Hi-Hi | BOOL | DB309.DBX0.7 |  |  | High | Logic 1 | Y | Manual | Y |  | -
A5_LIT323_HI_ALM | Blind Tank Level - High | BOOL | DB309.DBX1.0 |  |  | Medium | Logic 1 | Y | Auto | Y |  | -
A5_LIT323_LO_ALM | Blind Tank Level - Low | BOOL | DB309.DBX1.1 |  |  | Medium | Logic 1 | Y | Auto | Y |  | -
A5_LIT323_LOLO_ALM | Blind Tank Level - Lo-Lo | BOOL | DB309.DBX1.2 |  |  | High | Logic 1 | Y | Supervisory | Y |  | -
A5_LIT323_OTR_ALM | Blind Tank Level - Out Of Range | BOOL | DB309.DBX1.3 |  |  | High | Logic 1 | Y | Supervisory | Y |  | -
A5_LIT323_INST_FLT_ALM | Blind Tank Level - Inst Fault | BOOL | DB309.DBX1.4 |  |  | High | Logic 1 | Y | Auto | Y |  | -
A5_LIT323_NODE_FLT_ALM | Blind Tank Level - Node Fault | BOOL | DB309.DBX1.5 |  |  | High | Logic 1 | Y | Auto | Y |  | -
A5_LS316_ALM | Chemical Tank High High Level - Alarm | BOOL | DB309.DBX1.6 |  |  | Medium | Logic 1 | Y | Auto | Y |  | -
A5_AV508_NOT_AV_ALM | Chemical Tank Outlet Valve - Not Available | BOOL | DB309.DBX1.7 |  |  | High | Logic 1 | Y | Auto | Y |  | -
A5_AV508_FTO_ALM | Chemical Tank Outlet Valve - Failed To Open | BOOL | DB309.DBX2.0 |  |  | High | Logic 1 | Y | Auto | Y |  | -
A5_AV508_FTC_ALM | Chemical Tank Outlet Valve - Failed To Close | BOOL | DB309.DBX2.1 |  |  | High | Logic 1 | Y | Auto | Y |  | -
A5_AV508_SFLT_ALM | Chemical Tank Outlet Valve - Limit Switch Fault | BOOL | DB309.DBX2.2 |  |  | Medium | Logic 1 | Y | Manual | Y |  | -
A5_AV508_NODE_FLT_ALM | Chemical Tank Outlet Valve - Node Fault | BOOL | DB309.DBX2.3 |  |  | Medium | Logic 1 | Y | Manual | Y |  | -
A5_LS318_ALM | Chemical Dosing Pump PRV Catch Pot - Alarm | BOOL | DB309.DBX2.4 |  |  | Medium | Logic 1 | Y | Manual | Y |  | -
A5_FIT112_HIHI_ALM | Chemical Dosing Pump Delivery Flowmeter - Hi-Hi | BOOL | DB309.DBX2.5 |  |  | Medium | Logic 1 | Y | Manual | Y |  | -
A5_FIT112_HI_ALM | Chemical Dosing Pump Delivery Flowmeter - High | BOOL | DB309.DBX2.6 |  |  | Medium | Logic 1 | Y | Manual | Y |  | -
A5_FIT112_LO_ALM | Chemical Dosing Pump Delivery Flowmeter - Low | BOOL | DB309.DBX2.7 |  |  | Medium | Logic 1 | Y | Manual | Y |  | -
A5_FIT112_LOLO_ALM | Chemical Dosing Pump Delivery Flowmeter - Lo-Lo | BOOL | DB309.DBX3.0 |  |  | Medium | Logic 1 | Y | Manual | Y |  | -
A5_FIT112_OTR_ALM | Chemical Dosing Pump Delivery Flowmeter - Out Of Range | BOOL | DB309.DBX3.1 |  |  | Medium | Logic 1 | Y | Manual | Y |  | -
A5_FIT112_INST_FLT_ALM | Chemical Dosing Pump Delivery Flowmeter - Inst Fault | BOOL | DB309.DBX3.2 |  |  | Medium | Logic 1 | Y | Manual | Y |  | -
A5_FIT112_NODE_FLT_ALM | Chemical Dosing Pump Delivery Flowmeter - Node Fault | BOOL | DB309.DBX3.3 |  |  | Medium | Logic 1 | Y | Manual | Y |  | -
A5_LS319_ALM | Chemical Dosing Skid Drip Tray High Level - Alarm | BOOL | DB309.DBX3.4 |  |  | High | Logic 1 | Y | Manual | Y |  | -
A5_LS320_ALM | Chemical Dual Containment Catch Pot - Alarm | BOOL | DB309.DBX3.5 |  |  | Medium | Logic 1 | Y | Manual | Y |  | -
A5_LS321_ALM | Chemical Dosing Dual Containment Enclosure Level - Alarm | BOOL | DB309.DBX3.6 |  |  | Medium | Logic 1 | Y | Manual | Y |  | -
A5_LS317_ALM | Chemical Tank High Level - Alarm | BOOL | DB309.DBX3.7 |  |  | Medium | Logic 1 | Y | Manual | Y |  | -
A5_XS201_ALM | Emergency Eyewash 1 - Alarm | BOOL | DB309.DBX4.0 |  |  | Medium | Logic 1 | Y | Auto | Y |  | -
A5_XS202_ALM | Emergency Eyewash 2 - Alarm | BOOL | DB309.DBX4.1 |  |  | Medium | Logic 1 | Y | Auto | Y |  | -
A5_XS203_ALM | Emergency Shower - Alarm | BOOL | DB309.DBX4.2 |  |  | Medium | Logic 1 | Y | Manual | Y |  | -
A5_LS322_ALM | Emergency Shower Low Level Switch - Alarm | BOOL | DB309.DBX4.3 |  |  | Medium | Logic 1 | Y | Manual | Y |  | -
A5_LS324_ALM | Chemical Blind Tank High High - Alarm | BOOL | DB309.DBX4.4 |  |  | Medium | Logic 1 | Y | Manual | Y |  | -
A5_TS601_ALM | Emergency Shower Low Temperature Switch - Alarm | BOOL | DB309.DBX4.5 |  |  | Medium | Logic 1 | Y | Manual | Y |  | -
A5_P504_BUP_CTRL_ALM | Chemical Dosing Pump - Backup Control Active Alarm | BOOL | DB309.DBX4.6 |  |  | Medium | Logic 1 | Y | Supervisory | Y |  | -
A5_P504_DP_INP1_ALM | Chemical Dosing Pump - Drive Specific Input 1 Alarm | BOOL | DB309.DBX4.7 |  |  | Medium | Logic 1 | Y | Supervisory | Y |  | -
A5_P504_DP_INP2_ALM | Chemical Dosing Pump - Drive Specific Input 2 Alarm | BOOL | DB309.DBX5.0 |  |  | Medium | Logic 1 | Y | Auto | Y |  | -
A5_P504_DP_INP3_ALM | Chemical Dosing Pump - Drive Specific Input 3 Alarm | BOOL | DB309.DBX5.1 |  |  | Medium | Logic 1 | Y | Auto | Y |  | -
A5_P504_E_STOP_ALM | Chemical Dosing Pump - Emergency Stop Operated Alarm | BOOL | DB309.DBX5.2 |  |  | Medium | Logic 1 | Y | Auto | Y |  | -
A5_P504_FTR_ALM | Chemical Dosing Pump - Failed To Run Alarm | BOOL | DB309.DBX5.3 |  |  | Medium | Logic 1 | Y | Auto | Y |  | -
A5_P504_FTR_SP_ALM | Chemical Dosing Pump - Failed To Reach Setpoint Alarm | BOOL | DB309.DBX5.4 |  |  | Medium | Logic 1 | Y | Auto | Y |  | -
A5_P504_FTS_ALM | Chemical Dosing Pump - Failed To Stop Alarm | BOOL | DB309.DBX5.5 |  |  | Medium | Logic 1 | Y | Supervisory | Y |  | -
A5_P504_GEN_FLT_ALM | Chemical Dosing Pump - General Fault Alarm | BOOL | DB309.DBX5.6 |  |  | High | Logic 1 | Y | Auto | Y |  | -
A5_P504_NODE_FLT_ALM | Chemical Dosing Pump - Node Fault Alarm | BOOL | DB309.DBX5.7 |  |  | High | Logic 1 | Y | Auto | Y |  | -
A5_P504_NOT_AV_ALM | Chemical Dosing Pump - Not Available Alarm | BOOL | DB309.DBX6.0 |  |  | High | Logic 1 | Y | Auto | Y |  | -
A5_P504_S_INT1_ALM | Chemical Dosing Pump - Safety Interlock 1 Alarm | BOOL | DB309.DBX6.1 |  |  | High | Logic 1 | Y | Auto | Y |  | -
A5_P504_S_INT2_ALM | Chemical Dosing Pump - Safety Interlock 2 Alarm | BOOL | DB309.DBX6.2 |  |  | High | Logic 1 | Y | Auto | Y |  | -
A5_P504_VSD_ALM | Chemical Dosing Pump - VSD Fault Alarm | BOOL | DB309.DBX6.3 |  |  | Low | Logic 1 | Y | Auto | Y |  | -
MCC05_110V_FLD_ALM | MCC05110V SupplyHealthyState | BOOL | DB309.DBX6.4 |  |  | Medium | Logic 1 | Y | Auto | Y |  | -
MCC05_24V_A_ALM | MCC0524VA Chemical-SupplyAHealthyState | BOOL | DB309.DBX6.5 |  |  | Medium | Logic 1 | Y | Auto | Y |  | -
MCC05_24V_B_ALM | MCC0524VBChemical-SupplyBHealthyState | BOOL | DB309.DBX6.6 |  |  | Medium | Logic 1 | Y | Auto | Y |  | -
MCC05_MAINS_FLD_ALM | ChemicalMCC05MainsSupplyHealthyState | BOOL | DB309.DBX6.7 |  |  | Medium | Logic 1 | Y | Auto | Y |  | -
PLC05_BUP_ON_ALM | PLC05BackupControlEnabledState | BOOL | DB309.DBX7.0 |  |  | Medium | Logic 1 | Y | Auto | Y |  | -
Data Summary
|  |  | Protocol | Bit Data Count | Byte Data Count | Word Data Count | Double Word Data Count | Total Data Quantity (Bytes) being transferred
|  |  | Ethernet | 57 | 0 | 0 | 0 | 7

## Siemens Telemetry PLC DB
Project Title: United Utilities - Tyldesley UID PLC05 - Chemical Dosing
UUID: 80021608_02
Contract Title: System Integration
Document Title: Software Design Specification | [9 empty] | 2014-02-12
SDS Annexure
Telemetry Database
Modbus Address | Telemetry Outstation Source Address | Mapped Address (Telemetry PLC) | Source PLC Number | Source PLC Node Address | Source PLC DB Address | Data Type | PLC Tag | Description | Doc. Rev. | State 0 | State 1 | Range | Reference Document
- |  |  | PLC#05 | 10.173.248.82 | DB66.DBX0.0 | BOOL | A5-XS203 | DOSING CONTROL PLC WATCHDOG |  | FAILED | HEALTHY |  | P&ID
- |  |  | PLC#05 | 10.173.248.82 | DB66.DBX0.1 | BOOL | A5-TS601 | DOSING CONTROL PLC BATTERY LOW VOLTS |  | LOW | HEALTHY |  | P&ID
- |  |  | PLC#05 | 10.173.248.82 | DB66.DBX0.2 | BOOL | A5-LS322 | DOSING CONTROL PROFIBUS NETWORK 1 |  | FAILED | HEALTHY |  | P&ID
- |  |  | PLC#05 | 10.173.248.82 | DB66.DBX0.3 | BOOL | A5-XS202 | DOSING CONTROL CP02 MAINS SUPPLY |  | FAILED | HEALTHY |  | P&ID
- |  |  | PLC#05 | 10.173.248.82 | DB66.DBX0.4 | BOOL | A5-XS201 | DOSING CONTROL CP02 110V SUPPLY |  | FAILED | HEALTHY |  | P&ID
- |  |  | PLC#05 | 10.173.248.82 | DB66.DBX0.5 | BOOL |  | DOSING CONTROL CP02 24V SUPPLY A |  | FAILED | HEALTHY |  | P&ID
- |  |  | PLC#05 | 10.173.248.82 | DB66.DBX0.6 | BOOL |  | DOSING CONTROL CP02 24V SUPPLY B |  | FAILED | HEALTHY |  | P&ID
- |  |  | PLC#05 | 10.173.248.82 | DB66.DBX0.7 | BOOL |  | DOSING CONTROL CP02 BOTH 24V SUPPLIES |  | FAILED | HEALTHY |  | P&ID
- |  |  | PLC#05 | 10.173.248.82 | DB66.DBX1.0 | BOOL |  | DOSING CONTROL PLANT |  | OFFLINE | ON LINE |  | P&ID
- |  |  | PLC#05 | 10.173.248.82 | DB66.DBX1.1 | BOOL |  | DETENTION TANK PLANT |  | TRIPPED | NORMAL |  | P&ID
- |  |  | PLC#05 | 10.173.248.82 | DB66.DBX1.2 | BOOL |  | DOSING CONTROL PLANT |  | TRIPPED | NORMAL |  | P&ID
- |  |  | PLC#05 | 10.173.248.82 | DB66.DBX1.3 | BOOL |  | CHEMICAL STORAGE TANK -LEVEL INSTRUMENT |  | FAULT | HEALTHY |  | P&ID
- |  |  | PLC#05 | 10.173.248.82 | DB66.DBX1.4 | BOOL |  | CHEMICAL STORAGE TANK - LEVEL |  | HIGH HIGH | NORMAL |  | P&ID
- |  |  | PLC#05 | 10.173.248.82 | DB66.DBX1.5 | BOOL |  | CHEMICAL STORAGE TANK BUND - LEVEL |  | HIGH | NORMAL |  | P&ID
- |  |  | PLC#05 | 10.173.248.82 | DB66.DBX1.6 | BOOL |  | CHEMICAL BLIND TANK - LEVEL INSTRUMENT |  | FAULT | HEALTHY |  | P&ID
- |  |  | PLC#05 | 10.173.248.82 | DB66.DBX1.7 | BOOL |  | CHEMICAL BLIND TANK - LEVEL |  | NORMAL | NORMAL |  | P&ID
- |  |  | PLC#05 | 10.173.248.82 | DB66.DBD2 | REAL | A5-DERIVEDFLOWFROMLIT312 | Detention Tank Inlet Flow ( derived ) |  |  |  | 0 - xxx ltrs/s | P&ID
- |  |  | PLC#05 | 10.173.248.82 | DB66.DBD6 | REAL | A5-FIT112 | Chemical Dosing Flowmeter |  |  |  | 0 - 625 l/hr | P&ID
- |  |  | PLC#05 | 10.173.248.82 | DB66.DBD10 | REAL | A5-LIT315 | Chemical Storage Tank Level |  |  |  | 0 -100 % | P&ID
-
Data Summary
Protocol | Bit Data Count | Byte Data Count | Word Data Count | Double Word Data Count | Total Data quantity(Bytes) being transferred
Ethernet | 16 | 0 | 0 | 3 | 14
[14 empty] | DB Address | Modbus Address
[14 empty] | DB120.DBX1.0 | 30001.Bit 0
[14 empty] | DB120.DBX1.1 | 30001.Bit 1
[14 empty] | DB120.DBX1.2 | 30001.Bit 2
[14 empty] | DB120.DBX1.3 | 30001.Bit 3
[14 empty] | DB120.DBX1.4 | 30001.Bit 4
[14 empty] | DB120.DBX1.5 | 30001.Bit 5
[14 empty] | DB120.DBX1.6 | 30001.Bit 6
[14 empty] | DB120.DBX1.7 | 30001.Bit 7
[14 empty] | DB120.DBX0.0 | 30001.Bit 8
[14 empty] | DB120.DBX0.1 | 30001.Bit 9
[14 empty] | DB120.DBX0.2 | 30001.Bit 10
[14 empty] | DB120.DBX0.3 | 30001.Bit 11
[14 empty] | DB120.DBX0.4 | 30001.Bit 12
[14 empty] | DB120.DBX0.5 | 30001.Bit 13
[14 empty] | DB120.DBX0.6 | 30001.Bit 14
[14 empty] | DB120.DBX0.7 | 30001.Bit 15
[14 empty] | DB120.DBX3.0 | 30002.Bit 0
[14 empty] | DB120.DBX3.1 | 30002.Bit 1
[14 empty] | DB120.DBX3.2 | 30002.Bit 2
[14 empty] | DB120.DBX3.3 | 30002.Bit 3
[14 empty] | DB120.DBX3.4 | 30002.Bit 4
[14 empty] | DB120.DBX3.5 | 30002.Bit 5
[14 empty] | DB120.DBX3.6 | 30002.Bit 6
[14 empty] | DB120.DBX3.7 | 30002.Bit 7
[14 empty] | DB120.DBX2.0 | 30002.Bit 8
[14 empty] | DB120.DBX2.1 | 30002.Bit 9
[14 empty] | DB120.DBX2.2 | 30002.Bit 10
[14 empty] | DB120.DBX2.3 | 30002.Bit 11
[14 empty] | DB120.DBX2.4 | 30002.Bit 12
[14 empty] | DB120.DBX2.5 | 30002.Bit 13
[14 empty] | DB120.DBX2.6 | 30002.Bit 14
[14 empty] | DB120.DBX2.7 | 30002.Bit 15
[14 empty] | DB120.DBX5.0 | 30003.Bit 0
[14 empty] | DB120.DBX5.1 | 30003.Bit 1
[14 empty] | DB120.DBX5.2 | 30003.Bit 2
[14 empty] | DB120.DBX5.3 | 30003.Bit 3
[14 empty] | DB120.DBX5.4 | 30003.Bit 4
[14 empty] | DB120.DBX5.5 | 30003.Bit 5
[14 empty] | DB120.DBX5.6 | 30003.Bit 6
[14 empty] | DB120.DBX5.7 | 30003.Bit 7
[14 empty] | DB120.DBX4.0 | 30003.Bit 8
[14 empty] | DB120.DBX4.1 | 30003.Bit 9
[14 empty] | DB120.DBX4.2 | 30003.Bit 10
[14 empty] | DB120.DBX4.3 | 30003.Bit 11
[14 empty] | DB120.DBX4.4 | 30003.Bit 12
[14 empty] | DB120.DBX4.5 | 30003.Bit 13
[14 empty] | DB120.DBX4.6 | 30003.Bit 14
[14 empty] | DB120.DBX4.7 | 30003.Bit 15
[14 empty] | DB120.DBX7.0 | 30004.Bit 0
[14 empty] | DB120.DBX7.1 | 30004.Bit 1
[14 empty] | DB120.DBX7.2 | 30004.Bit 2
[14 empty] | DB120.DBX7.3 | 30004.Bit 3
[14 empty] | DB120.DBX7.4 | 30004.Bit 4
[14 empty] | DB120.DBX7.5 | 30004.Bit 5
[14 empty] | DB120.DBX7.6 | 30004.Bit 6
[14 empty] | DB120.DBX7.7 | 30004.Bit 7
[14 empty] | DB120.DBX6.0 | 30004.Bit 8
[14 empty] | DB120.DBX6.1 | 30004.Bit 9
[14 empty] | DB120.DBX6.2 | 30004.Bit 10
[14 empty] | DB120.DBX6.3 | 30004.Bit 11
[14 empty] | DB120.DBX6.4 | 30004.Bit 12
[14 empty] | DB120.DBX6.5 | 30004.Bit 13
[14 empty] | DB120.DBX6.6 | 30004.Bit 14
[14 empty] | DB120.DBX6.7 | 30004.Bit 15
[14 empty] | DB120.DBX9.0 | 30005.Bit 0
[14 empty] | DB120.DBX9.1 | 30005.Bit 1
[14 empty] | DB120.DBX9.2 | 30005.Bit 2
[14 empty] | DB120.DBX9.3 | 30005.Bit 3
[14 empty] | DB120.DBX9.4 | 30005.Bit 4
[14 empty] | DB120.DBX9.5 | 30005.Bit 5
[14 empty] | DB120.DBX9.6 | 30005.Bit 6
[14 empty] | DB120.DBX9.7 | 30005.Bit 7
[14 empty] | DB120.DBX8.0 | 30005.Bit 8
[14 empty] | DB120.DBX8.1 | 30005.Bit 9
[14 empty] | DB120.DBX8.2 | 30005.Bit 10
[14 empty] | DB120.DBX8.3 | 30005.Bit 11
[14 empty] | DB120.DBX8.4 | 30005.Bit 12
[14 empty] | DB120.DBX8.5 | 30005.Bit 13
[14 empty] | DB120.DBX8.6 | 30005.Bit 14
[14 empty] | DB120.DBX8.7 | 30005.Bit 15
[14 empty] | DB120.DBX11.0 | 30006.Bit 0
[14 empty] | DB120.DBX11.1 | 30006.Bit 1
[14 empty] | DB120.DBX11.2 | 30006.Bit 2
[14 empty] | DB120.DBX11.3 | 30006.Bit 3
[14 empty] | DB120.DBX11.4 | 30006.Bit 4
[14 empty] | DB120.DBX11.5 | 30006.Bit 5
[14 empty] | DB120.DBX11.6 | 30006.Bit 6
[14 empty] | DB120.DBX11.7 | 30006.Bit 7
[14 empty] | DB120.DBX10.0 | 30006.Bit 8
[14 empty] | DB120.DBX10.1 | 30006.Bit 9
[14 empty] | DB120.DBX10.2 | 30006.Bit 10
[14 empty] | DB120.DBX10.3 | 30006.Bit 11
[14 empty] | DB120.DBX10.4 | 30006.Bit 12
[14 empty] | DB120.DBX10.5 | 30006.Bit 13
[14 empty] | DB120.DBX10.6 | 30006.Bit 14
[14 empty] | DB120.DBX10.7 | 30006.Bit 15
[14 empty] | DB120.DBX13.0 | 30007.Bit 0
[14 empty] | DB120.DBX13.1 | 30007.Bit 1
[14 empty] | DB120.DBX13.2 | 30007.Bit 2
[14 empty] | DB120.DBX13.3 | 30007.Bit 3
[14 empty] | DB120.DBX13.4 | 30007.Bit 4
[14 empty] | DB120.DBX13.5 | 30007.Bit 5
[14 empty] | DB120.DBX13.6 | 30007.Bit 6
[14 empty] | DB120.DBX13.7 | 30007.Bit 7
[14 empty] | DB120.DBX12.0 | 30007.Bit 8
[14 empty] | DB120.DBX12.1 | 30007.Bit 9
[14 empty] | DB120.DBX12.2 | 30007.Bit 10
[14 empty] | DB120.DBX12.3 | 30007.Bit 11
[14 empty] | DB120.DBX12.4 | 30007.Bit 12
[14 empty] | DB120.DBX12.5 | 30007.Bit 13
[14 empty] | DB120.DBX12.6 | 30007.Bit 14
[14 empty] | DB120.DBX12.7 | 30007.Bit 15
[14 empty] | DB120.DBX15.0 | 30008.Bit 0
[14 empty] | DB120.DBX15.1 | 30008.Bit 1
[14 empty] | DB120.DBX15.2 | 30008.Bit 2
[14 empty] | DB120.DBX15.3 | 30008.Bit 3
[14 empty] | DB120.DBX15.4 | 30008.Bit 4
[14 empty] | DB120.DBX15.5 | 30008.Bit 5
[14 empty] | DB120.DBX15.6 | 30008.Bit 6
[14 empty] | DB120.DBX15.7 | 30008.Bit 7
[14 empty] | DB120.DBX14.0 | 30008.Bit 8
[14 empty] | DB120.DBX14.1 | 30008.Bit 9
[14 empty] | DB120.DBX14.2 | 30008.Bit 10
[14 empty] | DB120.DBX14.3 | 30008.Bit 11
[14 empty] | DB120.DBX14.4 | 30008.Bit 12
[14 empty] | DB120.DBX14.5 | 30008.Bit 13
[14 empty] | DB120.DBX14.6 | 30008.Bit 14
[14 empty] | DB120.DBX14.7 | 30008.Bit 15
[14 empty] | DB120.DBX17.0 | 30009.Bit 0
[14 empty] | DB120.DBX17.1 | 30009.Bit 1
[14 empty] | DB120.DBX17.2 | 30009.Bit 2
[14 empty] | DB120.DBX17.3 | 30009.Bit 3
[14 empty] | DB120.DBX17.4 | 30009.Bit 4
[14 empty] | DB120.DBX17.5 | 30009.Bit 5
[14 empty] | DB120.DBX17.6 | 30009.Bit 6
[14 empty] | DB120.DBX17.7 | 30009.Bit 7
[14 empty] | DB120.DBX16.0 | 30009.Bit 8
[14 empty] | DB120.DBX16.1 | 30009.Bit 9
[14 empty] | DB120.DBX16.2 | 30009.Bit 10
[14 empty] | DB120.DBX16.3 | 30009.Bit 11
[14 empty] | DB120.DBX16.4 | 30009.Bit 12
[14 empty] | DB120.DBX16.5 | 30009.Bit 13
[14 empty] | DB120.DBX16.6 | 30009.Bit 14
[14 empty] | DB120.DBX16.7 | 30009.Bit 15
[14 empty] | DB120.DBX19.0 | 30010.Bit 0
[14 empty] | DB120.DBX19.1 | 30010.Bit 1
[14 empty] | DB120.DBX19.2 | 30010.Bit 2
[14 empty] | DB120.DBX19.3 | 30010.Bit 3
[14 empty] | DB120.DBX19.4 | 30010.Bit 4
[14 empty] | DB120.DBX19.5 | 30010.Bit 5
[14 empty] | DB120.DBX19.6 | 30010.Bit 6
[14 empty] | DB120.DBX19.7 | 30010.Bit 7
[14 empty] | DB120.DBX18.0 | 30010.Bit 8
[14 empty] | DB120.DBX18.1 | 30010.Bit 9
[14 empty] | DB120.DBX18.2 | 30010.Bit 10
[14 empty] | DB120.DBX18.3 | 30010.Bit 11
[14 empty] | DB120.DBX18.4 | 30010.Bit 12
[14 empty] | DB120.DBX18.5 | 30010.Bit 13
[14 empty] | DB120.DBX18.6 | 30010.Bit 14
[14 empty] | DB120.DBX18.7 | 30010.Bit 15
[14 empty] | DB120.DBX21.0 | 30011.Bit 0
[14 empty] | DB120.DBX21.1 | 30011.Bit 1
[14 empty] | DB120.DBX21.2 | 30011.Bit 2
[14 empty] | DB120.DBX21.3 | 30011.Bit 3
[14 empty] | DB120.DBX21.4 | 30011.Bit 4
[14 empty] | DB120.DBX21.5 | 30011.Bit 5
[14 empty] | DB120.DBX21.6 | 30011.Bit 6
[14 empty] | DB120.DBX21.7 | 30011.Bit 7
[14 empty] | DB120.DBX20.0 | 30011.Bit 8
[14 empty] | DB120.DBX20.1 | 30011.Bit 9
[14 empty] | DB120.DBX20.2 | 30011.Bit 10
[14 empty] | DB120.DBX20.3 | 30011.Bit 11
[14 empty] | DB120.DBX20.4 | 30011.Bit 12
[14 empty] | DB120.DBX20.5 | 30011.Bit 13
[14 empty] | DB120.DBX20.6 | 30011.Bit 14
[14 empty] | DB120.DBX20.7 | 30011.Bit 15
[14 empty] | DB120.DBX23.0 | 30012.Bit 0
[14 empty] | DB120.DBX23.1 | 30012.Bit 1
[14 empty] | DB120.DBX23.2 | 30012.Bit 2
[14 empty] | DB120.DBX23.3 | 30012.Bit 3
[14 empty] | DB120.DBX23.4 | 30012.Bit 4
[14 empty] | DB120.DBX23.5 | 30012.Bit 5
[14 empty] | DB120.DBX23.6 | 30012.Bit 6
[14 empty] | DB120.DBX23.7 | 30012.Bit 7
[14 empty] | DB120.DBX22.0 | 30012.Bit 8
[14 empty] | DB120.DBX22.1 | 30012.Bit 9
[14 empty] | DB120.DBX22.2 | 30012.Bit 10
[14 empty] | DB120.DBX22.3 | 30012.Bit 11
[14 empty] | DB120.DBX22.4 | 30012.Bit 12
[14 empty] | DB120.DBX22.5 | 30012.Bit 13
[14 empty] | DB120.DBX22.6 | 30012.Bit 14
[14 empty] | DB120.DBX22.7 | 30012.Bit 15
[14 empty] | DB120.DBX25.0 | 30013.Bit 0
[14 empty] | DB120.DBX25.1 | 30013.Bit 1
[14 empty] | DB120.DBX25.2 | 30013.Bit 2
[14 empty] | DB120.DBX25.3 | 30013.Bit 3
[14 empty] | DB120.DBX25.4 | 30013.Bit 4
[14 empty] | DB120.DBX25.5 | 30013.Bit 5
[14 empty] | DB120.DBX25.6 | 30013.Bit 6
[14 empty] | DB120.DBX25.7 | 30013.Bit 7
[14 empty] | DB120.DBX24.0 | 30013.Bit 8
[14 empty] | DB120.DBX24.1 | 30013.Bit 9
[14 empty] | DB120.DBX24.2 | 30013.Bit 10
[14 empty] | DB120.DBX24.3 | 30013.Bit 11
[14 empty] | DB120.DBX24.4 | 30013.Bit 12
[14 empty] | DB120.DBX24.5 | 30013.Bit 13
[14 empty] | DB120.DBX24.6 | 30013.Bit 14
[14 empty] | DB120.DBX24.7 | 30013.Bit 15
[14 empty] | DB120.DBX27.0 | 30014.Bit 0
[14 empty] | DB120.DBX27.1 | 30014.Bit 1
[14 empty] | DB120.DBX27.2 | 30014.Bit 2
[14 empty] | DB120.DBX27.3 | 30014.Bit 3
[14 empty] | DB120.DBX27.4 | 30014.Bit 4
[14 empty] | DB120.DBX27.5 | 30014.Bit 5
[14 empty] | DB120.DBX27.6 | 30014.Bit 6
[14 empty] | DB120.DBX27.7 | 30014.Bit 7
[14 empty] | DB120.DBX26.0 | 30014.Bit 8
[14 empty] | DB120.DBX26.1 | 30014.Bit 9
[14 empty] | DB120.DBX26.2 | 30014.Bit 10
[14 empty] | DB120.DBX26.3 | 30014.Bit 11
[14 empty] | DB120.DBX26.4 | 30014.Bit 12
[14 empty] | DB120.DBX26.5 | 30014.Bit 13
[14 empty] | DB120.DBX26.6 | 30014.Bit 14
[14 empty] | DB120.DBX26.7 | 30014.Bit 15
[14 empty] | DB120.DBX29.0 | 30015.Bit 0
[14 empty] | DB120.DBX29.1 | 30015.Bit 1
[14 empty] | DB120.DBX29.2 | 30015.Bit 2
[14 empty] | DB120.DBX29.3 | 30015.Bit 3
[14 empty] | DB120.DBX29.4 | 30015.Bit 4
[14 empty] | DB120.DBX29.5 | 30015.Bit 5
[14 empty] | DB120.DBX29.6 | 30015.Bit 6
[14 empty] | DB120.DBX29.7 | 30015.Bit 7
[14 empty] | DB120.DBX28.0 | 30015.Bit 8
[14 empty] | DB120.DBX28.1 | 30015.Bit 9
[14 empty] | DB120.DBX28.2 | 30015.Bit 10
[14 empty] | DB120.DBX28.3 | 30015.Bit 11
[14 empty] | DB120.DBX28.4 | 30015.Bit 12
[14 empty] | DB120.DBX28.5 | 30015.Bit 13
[14 empty] | DB120.DBX28.6 | 30015.Bit 14
[14 empty] | DB120.DBX28.7 | 30015.Bit 15
[14 empty] | DB120.DBX31.0 | 30016.Bit 0
[14 empty] | DB120.DBX31.1 | 30016.Bit 1
[14 empty] | DB120.DBX31.2 | 30016.Bit 2
[14 empty] | DB120.DBX31.3 | 30016.Bit 3
[14 empty] | DB120.DBX31.4 | 30016.Bit 4
[14 empty] | DB120.DBX31.5 | 30016.Bit 5
[14 empty] | DB120.DBX31.6 | 30016.Bit 6
[14 empty] | DB120.DBX31.7 | 30016.Bit 7
[14 empty] | DB120.DBX30.0 | 30016.Bit 8
[14 empty] | DB120.DBX30.1 | 30016.Bit 9
[14 empty] | DB120.DBX30.2 | 30016.Bit 10
[14 empty] | DB120.DBX30.3 | 30016.Bit 11
[14 empty] | DB120.DBX30.4 | 30016.Bit 12
[14 empty] | DB120.DBX30.5 | 30016.Bit 13
[14 empty] | DB120.DBX30.6 | 30016.Bit 14
[14 empty] | DB120.DBX30.7 | 30016.Bit 15
[14 empty] | DB121.DBW0 | 30512
[14 empty] | DB121.DBW2 | 30513
[14 empty] | DB121.DBW4 | 30514
[14 empty] | DB121.DBW6 | 30515
[14 empty] | DB121.DBW8 | 30516
[14 empty] | DB121.DBW10 | 30517
[14 empty] | DB121.DBW12 | 30518
[14 empty] | DB121.DBW14 | 30519
[14 empty] | DB121.DBW16 | 30520
[14 empty] | DB121.DBW18 | 30521
[14 empty] | DB121.DBW20 | 30522
[14 empty] | DB121.DBW22 | 30523
[14 empty] | DB121.DBW24 | 30524
[14 empty] | DB121.DBW26 | 30525
[14 empty] | DB121.DBW28 | 30526
[14 empty] | DB121.DBW30 | 30527
[14 empty] | DB121.DBW32 | 30528
[14 empty] | DB121.DBW34 | 30529
[14 empty] | DB121.DBW36 | 30530
[14 empty] | DB121.DBW38 | 30531
[14 empty] | DB121.DBW40 | 30532
[14 empty] | DB121.DBW42 | 30533
[14 empty] | DB121.DBW44 | 30534
[14 empty] | DB121.DBW46 | 30535
[14 empty] | DB121.DBW48 | 30536
[14 empty] | DB121.DBW50 | 30537
[14 empty] | DB121.DBW52 | 30538
[14 empty] | DB121.DBW54 | 30539
[14 empty] | DB121.DBW56 | 30540
[14 empty] | DB121.DBW58 | 30541
[14 empty] | DB121.DBW60 | 30542
[14 empty] | DB121.DBW62 | 30543
[14 empty] | DB121.DBW64 | 30544
[14 empty] | DB121.DBW66 | 30545
[14 empty] | DB121.DBW68 | 30546
[14 empty] | DB121.DBW70 | 30547
[14 empty] | DB121.DBW72 | 30548
[14 empty] | DB121.DBW74 | 30549
[14 empty] | DB121.DBW76 | 30550
[14 empty] | DB121.DBW78 | 30551
[14 empty] | DB121.DBW80 | 30552
[14 empty] | DB121.DBW82 | 30553
[14 empty] | DB121.DBW84 | 30554
[14 empty] | DB121.DBW86 | 30555
[14 empty] | DB121.DBW88 | 30556
[14 empty] | DB121.DBW90 | 30557
[14 empty] | DB121.DBW92 | 30558
[14 empty] | DB121.DBW94 | 30559
[14 empty] | DB121.DBW96 | 30560
[14 empty] | DB121.DBW98 | 30561
[14 empty] | DB121.DBW100 | 30562
[14 empty] | DB121.DBW102 | 30563
[14 empty] | DB121.DBW104 | 30564
[14 empty] | DB121.DBW106 | 30565
[14 empty] | DB121.DBW108 | 30566
[14 empty] | DB121.DBW110 | 30567
[14 empty] | DB121.DBW112 | 30568
[14 empty] | DB121.DBW114 | 30569
[14 empty] | DB121.DBW116 | 30570
[14 empty] | DB121.DBW118 | 30571
[14 empty] | DB121.DBW120 | 30572

## Data (hidden)
Yes / No
Y
N
NA
Data type
BOOL
BYTE
WORD
DWORD
INT
DINT
REAL
Reset
Manual
Auto